## Key
IEEE 1815.2 Standard Profile Companion Data Point Tables: Version 1.1
DNP3 Points |  | Start Index | BO | BI | AO | AI | CTR
SCADA
Configuration & Control Points |  | 0 | 0 | 0 | 0 | 0 | 0
Functions |  | 0 | 12 | 31 | 22 | 71 | 0 |  | Configuration Settings
Curves | Max of 100 x,y pairs per Curve | 0 | 0 | 107 | 244 | 328 | 0 |  | Allocate the number of curves and the maximum number of points per curve
System Meter |  | 0 | 0 | 94 | 449 | 533 | 0
Extensions beyond DNP3 AN2018-001 |  | 0 | 42 | 108 | 461 | 569 | 0
Gap #1 | Reserved for future extensions | x | 44 | 111 | 476 | 586
Schedules
Schedules (2 items/step) | Time offset, value (for backwards compat) | 2000 | 2000 | 2000 | 2000 | 2000 |  |  | Allocate number of schedules and the maximum points per schedule
Schedule Status (2 items) | Schedule Status of first 100 | 2300 |  | 2300 |  | 2300
Schedules (4 items/step) | Time offset, Action type, AO or BO Index, & Value | 3000 | 3000 | 3000 | 3000 | 3000
Schedule Status (4 items) | Schedule Status of first 100 | 3500 | - | 3500 | - | 3500
Gap #2 | Reserved for future extensions | 4000
Equipment Points |  |  | BO | BI | AO | AI | CTR | Enter Maximum # of Devices
Meters | Start of additional meter points | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 1 | No. of Meters
| mh(1) set of points per meter |  | 0 | 13 | 12 | 37 | 4
| mh(n) total length of points |  | 0 | 39 | 36 | 111 | 12
DER Units | Start of DER unit points. | 10000 | 10000 | 10000 | 10000 | 10000 |  | 1 | No. DER Units
| duh(1) set of points per DER unit |  | 0 | 4 | 0 | 15 | 0
| duh(n) total length of points |  | 0 | 28 | 0 | 98
Inverters | Start of inverter points. | 15000 | 15000 | 15000 | 15000 | 15000 |  | 1 | No. Inverters
| ihh(1) set of points per inverter |  | 0 | 35 | 12 | 34 | 0
| ihh(n) total length of points |  | 0 | 70 | 24 | 66
Batteries | Start of battery points. | 20000 | 20000 | 20000 | 20000 | 20000 |  | 1 | No. Batteries
| bhh(1) set of points per battery |  | 0 | 54 | 4 | 28 | 0 | For each meter, DER unit, inverter, and battery, additional historical data rows need to be added in the spreadsheet to define the actual points
| bhh(n) total length of points |  | 0 | 108 | 8 | 54
Experimental Extensions | Reserved for experimental extensions | 30000
Vendor Points (VP) |  | 50000 | 50000 | 50000 | 50000 | 50000 |  | State if Storage
Start Index Points | Used for optional Auto Discovery | 60000 |  |  |  | 60000 |  | Yes | Storage? Yes or No
Maximum Index Value |  | 65535
mhbi(n) | Starting index of meter #n binary inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhbi(n) | Starting index of DER unit #n binary inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihbi(n) | Starting index of inverter #n binary inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhbi(n) | Starting index of battery #n binary inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhai(n) | Starting index of meter #n analog inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhai(n) | Starting index of DER unit #n analog inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihai(n) | Starting index of inverter #n analog inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhai(n) | Starting index of battery #n analog inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhao(n) | Starting index of meter #n analog outputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
ihao(n) | Starting index of inverter #n analog outputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhao(n) | Starting index of battery #n analog outputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)

## BO
DNP3 Point Index | Name / Description | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  |  |  | IEC61850UniqueString | Assoc. BI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BO0 | System Set Lockout State | Not Locked Out | Lock Out | DSTO.DEROpSt.disconnectedandblocked | BI11 | State | M
BO1 | System Initiate Start-up Sequence (Return to Service) | No Change | Initiate Start-up | DCTE.CeaEgzReqCtl.2 | BI12 | State | M
BO2 | System Execute Stop (Cease to Energize) | No Change | Stop (Emergency) | DCTE.CeaEgzReqCtl.1 | BI15 | State | M
BO3 | System Permission to Start | Start Permission Not Granted | Start Permission Granted | DGEN.PrmConn | BI16 | Enter Service | M | M
BO4 | System Permission to Stop | Stop Permission Not Granted | Stop Permission Granted | DGEN.PrmDscon | BI17 | Enter Service
BO5 | DER Connect/Disconnect Switch | Open Switch | Close Switch | CSWI.Pos | BI23 | Monitoring
BO6 | Islanded Mode. Determines how the DER behaves when in an Islanded configuration. <0> Isochronous Mode. DER attempts to control voltage and frequency independent of configured curves and settings up to the limits of the machine's capabilities in order to achieve AO reference voltage and AO nominal frequency. <1> Droop Mode. DER acts as a follower using Volt/Var and Freq/Watt curves. | Isochronous Mode | Droop Mode | DGEN.IsldCtlFol | BI25 | State | C: If in microgrid configuration
BO7 | Enable Sensed Grid Config Detection. If Enabled, the DER may independently change its Active Settings Group based on locally observed grid conditions. <0> No Autonomous Detection. <1> Autonomous Detection. Inverter's Active Settings Group may differ from the Requested Settings Group | No Autonomous Detection | Autonomous Detection | DECP.ECPIsldAuto | BI26 | State | C: If in microgrid configuration
BO8 | Storage Capacity Units. Determines whether the energy storage values are expressed in Amp-hrs or Watt-hrs. | Amp-hrs | Watt-hrs | DSTO.AGra | BI27 | State
BO9 | Time Constant Mode. Indicates whether Time Constant Ramp parameters are interpreted as Open Loop Response times or 3Tau values. | Open Loop Response Time | 3Tau Value | DGEN.OpnLoopTau | BI28 | State
BO10 | Power Factor Excitation When Discharging/Generating | Producing Vars - Q1 | Absorbing Vars - Q4 | DFPF.PFGnExtSet | BI29 | State
BO11 | Power Factor Excitation When Charging | Producing Vars - Q2 | Absorbing Vars - Q3 | DFPF.PFLodExtSet | BI30 | State
BO12 | Enable Low/High Voltage Ride-Through Mode | Disable | Enable | DHVT.Mod | BI64 | Volt Ride-Through | C: For Function
BO13 | Enable Low/High Frequency Ride-Through Mode | Disable | Enable | DHFT.Mod | BI65 | Freq Ride-Through | C: For Function
BO14 | Enable Dynamic Reactive Current Support Mode | Disable | Enable | DRGS.Mod | BI66 | Dyn React Curr Supp | C: For Function
BO15 | Enable Dynamic Volt-Watt Mode | Disable | Enable | DVWD.Mod | BI67 | Dyn Volt-Watt | C: For Function
BO16 | Enable Frequency-Watt Droop Mode | Disable | Enable | DHFW1.Mod | BI68 | Freq-Watt | C: For Function
BO17 | Enable Active Power Limit Mode | Disable | Enable | DWMX.Mod | BI69 | Active Power Limit | C: For Function | M
BO18 | Enable Charge/Discharge Mode | Disable | Enable | DWGC.Mod | BI70 | Set Active Power | C: For Function
BO19 | Enable Coordinated Charge/Discharge Mode | Disable | Enable | DTCD.Mod | BI71 | Coord Charge-Dischg | C: For Function
BO20 | Enable Active Power Following Mode #1 (Peak Power Limiting) | Disable | Enable | DWFL1.Mod | BI72 | Peak Power Limiting | C: For Function
BO21 | Enable Active Power Following Mode #2 (Load Following) | Disable | Enable | DWFL2.Mod | BI73 | Load Following | C: For Function
BO22 | Enable Active Power Following Mode #3 (Generation Following) | Disable | Enable | DWFL3.Mod | BI74 | Generation Following | C: For Function
BO23 | Enable Automatic Generation Control Mode | Disable | Enable | DAGC.Mod | BI75 | AGC | C: For Function
BO24 | Enable Active Power Smoothing Mode | Disable | Enable | DWSM.Mod | BI76 | Active Power Smoothing | C: For Function
BO25 | Enable Volt-Watt Mode | Disable | Enable | DVWC.Mod | BI77 | Volt-Watt | C: For Function | M
BO26 | Enable Frequency-Watt Curve Mode | Disable | Enable | DHFW2.Mod | BI78 | Freq-Watt Curve | C: For Function
BO27 | Enable Constant Vars Mode | Disable | Enable | DVAR.Mod | BI79 | Const Vars | C: For Function | M
BO28 | Enable Constant Power Factor Mode | Disable | Enable | DFPF.Mod | BI80 | Constant PF | C: For Function | M
BO29 | Enable Volt-Var Control Mode | Disable | Enable | DVVR.Mod | BI81 | Volt-Var | C: For Function | M
BO30 | Enable Watt-Var Mode | Disable | Enable | DWVR.Mod | BI82 | Watt-Var | C: For Function
BO31 | Enable Power Factor Correction Mode | Disable | Enable | DPFC.Mod | BI83 | PF Correct | C: For Function
BO32 | Enable Pricing Mode | Disable | Enable | DPRG.Mod | BI84 | Price | C: For Function
BO33 | Enable Event-Based Reactive Current Support Mode. The moving average voltage and the base reactive current are frozen until after the voltage has returned to within the deadband for a specified hold time. Dynamic Reactive Current Support mode must be Enable for this setting to apply. | Disable | Enable | DRGS.ArGraMod | BI85 | Mode State | C: For Function
BO34 | Frequency-Watt Mode - Use Hysteresis | Disable | Enable | DHFW.HysEna | BI86 | Freq-Watt
BO35 | Frequency-Watt Mode - Snapshot of Power | Not Active | Active | DHFW.SnptEna | BI87 | Freq-Watt
BO36 | Frequency-Watt Curve Mode - Use Hysteresis | Disable | Enable | DHFW1.HysEna | BI88 | Freq-Watt Curve | C: For Function
BO37 | Frequency-Watt Curve Mode - Snapshot of Power | Not Active | Active | DHFW1.SnptEna | BI89 | Freq-Watt Curve | C: For Function
BO38 | Charge/Discharge Mode - Use Ramp Rates. Indicates whether or not Charge/Discharge should use specified ramp rates or time constants. | Use Time Constants | Use Ramp Rates | DWGC.UseRmpRte | BI90 | Set Active Power | C: For Function
BO39 | AGC Mode - Use Ramp Rates. Indicates whether or not AGC mode should use specified ramp rates or time constants. | Use Time Constants | Use Ramp Rates | DAGC.UseRmpRte | BI91 | AGC | C: For Function
BO40 | Volt-Watt - Use Ramp Rates and Time Constants. Indicates whether Volt-Watt mode should use only Time Constants, or both Time Constants and Ramp Rates | Use Time Constants | Use Ramp Rates AND Time Constants | DVWC.UseRmpRte | BI92 | Volt-Watt | C: For Function
BO41 | Volt-Var Enable Autonomous Voltage Reference Adjustment | Disable | Enable | DVVR.VRefAdjEna | BI93 | Volt-Var | C: For Function | M
BO43 | Enable Renewable Energy Charging | Disable | Enable | DREN.Mod | BI110 | Renewable energy charging | C: For Function
BO44 | Enable Frequency-Watt Droop Function. Use Watts per Hz | Percent | Watts | DHFW3.Mod | BI112 | Droop Freq-Watt | C: For Function if Type is modifiable | M as watts
BO45 | Set Type of Active Power Limit. Use Percent or Watts | Percent | Watts | DWMX1.Mod | BI113 | Active Power Limit | C: For Function if Type is modifiable
BO46 | Set Type of Charge/Discharge target to % WMax or to Watts | Percent | Watts | DWGC1.Mod | BI114 | Charge/Discharge | C: For Function if Type is modifiable
BO47 | Set Constant Vars to use percent or vars | Percent | Vars | DVAR.1Mod | BI115 | Constant Vars | C: For Function if Type is modifiable | M as vars
BO2000 | Selected Schedule is Ready | Disable | Enable | BC.FSCHn.SchdSt.3 | BI2000 | BC Scheduling | C: If Back Comp Scheduling is used
BO2001 | Set Selected Schedule Repeat Weekly Sunday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.1 | BI2001 | BC Scheduling | C: If Back Comp Scheduling is used
BO2002 | Set Selected Schedule Repeat Weekly Monday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.2 | BI2002 | BC Scheduling | C: If Back Comp Scheduling is used
BO2003 | Set Selected Schedule Repeat Weekly Tuesday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.3 | BI2003 | BC Scheduling | C: If Back Comp Scheduling is used
BO2004 | Set Selected Schedule Repeat Weekly Wednesday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.4 | BI2004 | BC Scheduling | C: If Back Comp Scheduling is used
BO2005 | Set Selected Schedule Repeat Weekly Thursday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.5 | BI2005 | BC Scheduling | C: If Back Comp Scheduling is used
BO2006 | Set Selected Schedule Repeat Weekly Friday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.6 | BI2006 | BC Scheduling | C: If Back Comp Scheduling is used
BO2007 | Set Selected Schedule Repeat Weekly Saturday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.7 | BI2007 | BC Scheduling | C: If Back Comp Scheduling is used
BO3000 | Submit Selected Schedule for Validation | Not Submitted | Submitted | FSCHn.SchdSt.2 | BI3000 | Scheduling | C: If 1815.2 Sched is used
BO3001 | Enable Selected Schedule | Disable | Enable | FSCHn.SchdSt.3 | BI3001 | Scheduling | C: If 1815.2 Sched is used
BO3002 | Set Selected Schedule Repeat Weekly Sunday | Do Not Repeat | Repeat | FSCHn.SchdReuse.1 | BI3002 | Scheduling | C: If 1815.2 Sched is used
BO3003 | Set Selected Schedule Repeat Weekly Monday | Do Not Repeat | Repeat | FSCHn.SchdReuse.2 | BI3003 | Scheduling | C: If 1815.2 Sched is used
BO3004 | Set Selected Schedule Repeat Weekly Tuesday | Do Not Repeat | Repeat | FSCHn.SchdReuse.3 | BI3004 | Scheduling | C: If 1815.2 Sched is used
BO3005 | Set Selected Schedule Repeat Weekly Wednesday | Do Not Repeat | Repeat | FSCHn.SchdReuse.4 | BI3005 | Scheduling | C: If 1815.2 Sched is used
BO3006 | Set Selected Schedule Repeat Weekly Thursday | Do Not Repeat | Repeat | FSCHn.SchdReuse.5 | BI3006 | Scheduling | C: If 1815.2 Sched is used
BO3007 | Set Selected Schedule Repeat Weekly Friday | Do Not Repeat | Repeat | FSCHn.SchdReuse.6 | BI3007 | Scheduling | C: If 1815.2 Sched is used
BO3008 | Set Selected Schedule Repeat Weekly Saturday | Do Not Repeat | Repeat | FSCHn.SchdReuse.7 | BI3008 | Scheduling | C: If 1815.2 Sched is used
BO30000 | Enable Volt-Watt Advanced Mode | Disable | Enable | DVWC1.Mod | BI30001 | Volt-Watt Advanced | C: For Function
BO30010 | Enable Synthetic Inertia Function | Disable | Enable | DSYN.Mod | BI30010 | Synthetic Inertia | C: For Function
VP | Vendor Points

## BI
DNP3 Point Index | Name / Description | Default Event Class | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Assoc. BO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BI0 | System Communication Error | 1 | Normal | Alarm: Communications error exists in the ESS | LCCH1.ChLiv |  | Alarm | M | M
BI1 | System Has Priority 1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH.GrAlm |  | Alarm | M | M
BI2 | System Has Priority 2 Alarms | 1 | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | CALH.GrWrn |  | Alarm
BI3 | System Has Priority 3 Alarms | 1 | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | CALH.GrInd |  | Alarm
BI4 | Storage State of Charge at Maximum. Maximum Usable State of Charge Reached. | 1 | Normal | Alarm | DSTO.SocHiWrn |  | Alarm
BI5 | Storage State of Charge is Too High. Maximum Reserve Percentage (of usable capacity) reached. | 1 | Normal | Alarm | DSTO.SocHiAlm |  | Alarm
BI6 | Storage State of Charge is Too Low. Minimum Reserve Percentage (of usable capacity) reached. | 1 | Normal | Alarm | DSTO.SocLoAlm |  | Alarm
BI7 | Storage State of Charge is Depleted. Minimum Usable State of Charge Reached. | 1 | Normal | Alarm | DSTO.SohLoAlm |  | Alarm
BI8 | Storage Internal Temperature is Too High | 1 | Normal | Alarm | DBAT.IntnTmpHiAlm |  | Alarm
BI9 | Storage External (Ambient) Temperature is Too High | 1 | Normal | Alarm | DBAT.ExtTmpHiAlm |  | Alarm
BI10 | System Is In Local State. System has been locked by a local operator which prevents other operators from executing commands. Note: Local State is also sometimes referred to as Maintenance State. Local State overrides Lockout State. | 2 | System not in local state | System in local state | DGEN.DEROpSt.disconnectedandinmaintenance |  | State
BI11 | System Is In Lockout State. System has been locked by an operator such that other operators may not execute commands. Lockout State is also sometimes referred to as Blocked State | 2 | System not locked out | System locked out | DSTO.DEROpSt.disconnectedandblocked | BO0 | State
BI12 | System Is Starting Up. Set to 1 when a BO "System Initiate Start-up Sequence" command has been received. | 2 | Not Starting Up | Start command has been received. | DCTE.CeaEgzReqSt.6 | BO1 | State
BI13 | System Is Stopping. Set to 1 when an BO "System Execute Stop" command has been received. | 2 | Not Stopping | Emergency stop command has been received. | DCTE.CeaEgzReqSt.3 |  | State
BI14 | System is Started (Return to Service). If any of the DER Units are started, then true. DER Units in the maintenance operational state are excluded. | 2 | Null | Started | DGEN.DEROpSt.synchronizing |  | State
BI15 | System is Stopped (Cease to Energize). If all of the DER Units are stopped, then true. DER Units in the maintenance operational state are excluded. | 2 | Null | Stopped | DGEN.DEROpSt.onbutdisconnectedandnotready | BO2 | State
BI16 | System Permission to Start Status | 2 | Start Permission Not Granted | Start Permission Granted | DGEN.PrmConn | BO3 | Enter Service
BI17 | System Permission to Stop Status | 2 | Stop Permission Not Granted | Stop Permission Granted | DGEN.PrmDscon | BO4 | Enter Service
BI18 | DER is Connected and Idle | 2 | Null | Idle-Connected | DGEN.DEROpSt.running |  | Monitoring
BI19 | DER is Connected and Generating | 2 | Null | On-Connected | DGEN.DEROpSt.connectedandgenerating |  | Monitoring
BI20 | DER is Connected and Charging | 2 | Null | On-Charging-Connected | DSTO.DEROpSt.connectedandconsuming |  | Monitoring
BI21 | DER is Off but Available to Start | 2 | Null | Off-Available | DGEN.DEROpSt.disconnectedandavailable |  | Monitoring | M | M
BI22 | DER is Off and Not Available to Start | 2 | Null | Off-Not-Available | DGEN.DEROpSt.disconnectedandblocked |  | Monitoring | M | M
BI23 | DER Connect/Disconnect Switch Closed Status | 2 | Open | Closed | CSWI.Pos.1 | BO5 | Monitoring
BI24 | DER Connect/Disconnect Switch Movement Status | 2 | Not Moving | Moving | CSWI.Pos.2 |  | Monitoring
BI25 | Islanded Mode. Determines how the DER behaves when in an Islanded configuration. <0> Isochronous Mode. DER attempts to control voltage and frequency independent of configured curves and settings up to the limits of the machine's capabilities in order to achieve the AO Reference Voltage and AO nominal frequency. <1> Droop Mode. DER acts as a follower using Volt/VAR and Freq/Watt curves. | 3 | Isochronous Mode | Droop Mode | DGEN.IsldCtlFol | BO6 | State | C: If in microgrid configuration
BI26 | Sensed Grid Config Detection Enabled. If Enabled, the DER may independently change its Active Settings Group based on locally observed grid conditions. <0> No Autonomous Detection. <1> Autonomous Detection. Inverter's Active Settings Group may differ from the Requested Settings Group | 3 | Not Ready | Ready | DECP.ECPIsldAuto | BO7 | State | C: If in microgrid configuration
BI27 | Storage Capacity Units. Determines whether energy storage values are expressed in units of Amp-hrs or Watt-hrs. | 3 | Amp-hrs (default) | Watt-hrs | DSTO.AGra | BO8 | State | C: For Storage
BI28 | Time Constant Mode. Indicates whether Time Constant Ramp parameters are interpreted as Open Loop Response times or 3Tau values. | 3 | Open Loop Response Time | 3Tau Value | DGEN.OpnLoopTau | BO9 | State
BI29 | Power Factor Excitation When Discharging / Generating | 2 | Injecting VARs - Q1 | Absorbing VARs - Q4 | DFPF.PFGnExtSet | BO10 | State | M
BI30 | Power Factor Excitation When Charging | 2 | Injecting VARs - Q2 | Absorbing VARs - Q3 | DFPF.PFLodExtSet | BO11 | State | M
BI31 | Supports Low/High Voltage Ride-Through Mode | 0 | Not Supported | Supported | DHVT |  | Volt Ride-Through | M | M
BI32 | Supports Low/High Frequency Ride-Through Mode | 0 | Not Supported | Supported | DHFT |  | Freq Ride-Through | M | M
BI33 | Supports Dynamic Reactive Current Support Mode | 0 | Not Supported | Supported | DRGS |  | Dyn React Curr Supp | M
BI34 | Supports Dynamic Volt-Watt Mode | 0 | Not Supported | Supported | DVWD |  | Dyn Volt-Watt | M
BI35 | Supports Frequency-Watt Mode | 0 | Not Supported | Supported | DHFW |  | Freq-Watt | M | M
BI36 | Supports Active Power Limit Mode | 0 | Not Supported | Supported | DWMX |  | Active Power Limit | M | M
BI37 | Supports Charge/Discharge Mode | 0 | Not Supported | Supported | DWGC |  | Set Active Power | M
BI38 | Supports Coordinated Charge/Discharge Mode | 0 | Not Supported | Supported | DTCD |  | Coord Charge-Dischg | M
BI39 | Supports Active Power Response Mode #1 (Peak Power Limiting) | 0 | Not Supported | Supported | DWFL1 |  | Peak Power Limiting | M
BI40 | Supports Active Power Response Mode #2 (Load Following) | 0 | Not Supported | Supported | DWFL2 |  | Load Following | M
BI41 | Supports Active Power Response Mode #3 (Generation Following) | 0 | Not Supported | Supported | DWFL3 |  | Generation Following | M
BI42 | Supports Automatic Generation Control Mode | 0 | Not Supported | Supported | DAGC |  | AGC | M
BI43 | Supports Active Power Smoothing Mode | 0 | Not Supported | Supported | DWSM |  | Active Power Smoothing | M
BI44 | Supports Volt-Watt Mode | 0 | Not Supported | Supported | DVWC |  | Volt-Watt | M | M
BI45 | Supports Frequency-Watt Curve Mode | 0 | Not Supported | Supported | DFWC |  | Freq-Watt Curve | M
BI46 | Supports Constant VArs Mode | 0 | Not Supported | Supported | DVAR |  | Const Vars | M | M
BI47 | Supports Constant Power Factor Mode | 0 | Not Supported | Supported | DFPF |  | Constant PF | M | M
BI48 | Supports Volt-VAr Control Mode | 0 | Not Supported | Supported | DVVR |  | Volt-Var | M | M
BI49 | Supports Watt-VAr Mode | 0 | Not Supported | Supported | DWVR |  | Watt-Var | M | M
BI50 | Supports Power Factor Correction Mode | 0 | Not Supported | Supported | DPFC |  | PF Correct | M
BI51 | Supports Pricing Mode | 0 | Not Supported | Supported | DPRG |  | Price | M
BI52 | Overvoltage Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTOV.Blk |  | Prot State | M
BI53 | Overvoltage Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTOV.Str.general |  | Prot State | M
BI54 | Overvoltage Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTOV.Op.general |  | Prot State | M
BI55 | Undervoltage Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTUV.Blk |  | Prot State | M
BI56 | Undervoltage Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTUV.Str.general |  | Prot State | M
BI57 | Undervoltage Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTUV.Op.general |  | Prot State | M
BI58 | Over Frequency Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTOF.Blk |  | Prot State | M
BI59 | Over Frequency Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTOF.Str.general |  | Prot State | M
BI60 | Over Frequency Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTOF.Op.general |  | Prot State | M
BI61 | Under Frequency Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTUF.Blk |  | Prot State | M
BI62 | Under Frequency Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTUF.Str.general |  | Prot State | M
BI63 | Under Frequency Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTUF.Op.general |  | Prot State | M
BI64 | Operating Mode - Low/High Voltage Ride-Through | 2 | Disabled | Enabled | DHVT.Mod | BO12 | Volt Ride-Through | C: For Function
BI65 | Operating Mode - Low/High Frequency Ride-Through | 2 | Disabled | Enabled | DHFT.Mod | BO13 | Freq Ride-Through | C: For Function
BI66 | Operating Mode - Dynamic Reactive Current Support Enabled | 2 | Disabled | Enabled | DRGS.Mod | BO14 | Dyn React Curr Supp | C: For Function
BI67 | Operating Mode - Dynamic Volt-Watt Enabled | 2 | Disabled | Enabled | DVWD.Mod | BO15 | Dyn Volt-Watt | C: For Function
BI68 | Operating Mode - Frequency-Watt Enabled | 2 | Disabled | Enabled | DHFW1.Mod | BO16 | Freq-Watt | C: For Function
BI69 | Operating Mode - Active Power Limit Enabled | 2 | Disabled | Enabled | DWMX.Mod | BO17 | Active Power Limit | C: For Function | M
BI70 | Operating Mode - Charge/Discharge Enabled | 2 | Disabled | Enabled | DWGC.Mod | BO18 | Set Active Power | C: For Function
BI71 | Operating Mode - Coordinated Charge / Discharge Management Enabled | 2 | Disabled | Enabled | DTCD.Mod | BO19 | Coord Charge-Dischg | C: For Function
BI72 | Operating Mode - Active Power Following Mode #1 (Peak Power Limiting) Enabled | 2 | Disabled | Enabled | DWFL1.Mod | BO20 | Peak Power Limiting | C: For Function
BI73 | Operating Mode - Active Power Following Mode #2 (Load Following) Enabled | 2 | Disabled | Enabled | DWFL2.Mod | BO21 | Load Following | C: For Function
BI74 | Operating Mode - Active Power Following Mode #3 (Generation Following) Enabled | 2 | Disabled | Enabled | DWFL3.Mod | BO22 | Generation Following | C: For Function
BI75 | Operating Mode - Automatic Generation Control Enabled | 2 | Disabled | Enabled | DAGC.Mod | BO23 | AGC | C: For Function
BI76 | Operating Mode - Active Power Smoothing Enabled | 2 | Disabled | Enabled | DWSM.Mod | BO24 | Active Power Smoothing | C: For Function
BI77 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWC.Mod | BO25 | Volt-Watt | C: For Function | M
BI78 | Operating Mode - Frequency-Watt Curve Enabled | 2 | Disabled | Enabled | DHFW2.Mod | BO26 | Freq-Watt Curve | C: For Function
BI79 | Operating Mode - Constant VArs Enabled | 2 | Disabled | Enabled | DVAR.Mod | BO27 | Const Vars | C: For Function | M
BI80 | Operating Mode - Constant Power Factor Enabled | 2 | Disabled | Enabled | DFPF.Mod | BO28 | Constant PF | C: For Function | M
BI81 | Operating Mode - Volt-VAR Control Enabled | 2 | Disabled | Enabled | DVVR.Mod | BO29 | Volt-Var | C: For Function | M
BI82 | Operating Mode - Watt-VAr Enabled | 2 | Disabled | Enabled | DWVR.Mod | BO30 | Watt-Var | C: For Function | M
BI83 | Operating Mode - Power Factor Correction Enabled | 2 | Disabled | Enabled | DPFC.Mod | BO31 | PF Correct | C: For Function
BI84 | Operating Mode - Pricing Enabled | 2 | Disabled | Enabled | DPRG.Mod | BO32 | Price | C: For Function
BI85 | Operating Mode - Event-Based Reactive Current Support Enabled | 2 | Disabled | Enabled | DRGS.ArGraMod | BO33 | Mode State | C: For Function
BI86 | Frequency-Watt Mode - Use Hysteresis | 2 | Disabled | Enabled | DHFW.HysEna | BO34 | Freq-Watt
BI87 | Frequency-Watt Mode - Snapshot of Power | 2 | Not Active | Active | DHFW.SnptEna | BO35 | Freq-Watt
BI88 | Frequency-Watt Curve Mode - Use Hysteresis | 2 | Disabled | Enabled | DHFW1.HysEna | BO36 | Freq-Watt Curve
BI89 | Frequency-Watt Curve Mode - Snapshot of Power | 2 | Not Active | Active | DHFW1.SnptEna | BO37 | Freq-Watt Curve
BI90 | Charge/Discharge Mode - Use Ramp Rates. Indicates whether or not Charge/Discharge should use specified ramp rates or ramp times. | 2 | Use Time Constants | Use Ramp Rates | DWGC.UseRmpRte | BO38 | Set Active Power | C: For Function
BI91 | AGC Mode - Use Ramp Rates. Indicates whether or not charge/discharge should use specified ramp rates or ramp times. | 2 | Use Time Constants | Use Ramp Rates | DAGC.UseRmpRte | BO39 | AGC | C: For Function
BI92 | Volt-Watt - Use Ramp Rates and Time Constants | 2 | Use Time Constants | Use Ramp Rates AND Time Constants | DVWC.UseRmpRte | BO40 | Volt-Watt | C: For Function
BI93 | Volt-VAr Enable Autonomous Voltage Reference Adjustment | 2 | Disabled | Enabled | DVVR.VRefAdjEna | BO41 | Volt-Var | C: For Function
BI94 | System Meter Active Power is Too High | 1 | Normal | Alarm | SYS.MMXU.TotW.range.max |  | Alarm | M
BI95 | System Meter Active Power is Too Low | 1 | Normal | Alarm | SYS.MMXU.TotW.range.min |  | Alarm | M
BI96 | System Meter Reactive Power is Too High | 1 | Normal | Alarm | SYS.MMXU.TotVAr.range.max |  | Alarm | M
BI97 | System Meter Reactive Power is Too Low | 1 | Normal | Alarm | SYS.MMXU.TotVAr.range.min |  | Alarm | M
BI98 | System Meter Power Factor is Too High | 1 | Normal | Alarm | SYS.MMXU.TotPF.range.max |  | Alarm | M
BI99 | System Meter Power Factor is Too Low | 1 | Normal | Alarm | SYS.MMXU.TotPF.range.min |  | Alarm | M
BI100 | System Meter Phase A Voltage is Too High | 1 | Normal | Alarm | SYS.MMXU.PhV.phsA.range.max |  | Alarm | M
BI101 | System Meter Phase A Voltage is Too Low | 1 | Normal | Alarm | SYS.MMXU.PhV.phsA.range.min |  | Alarm | M
BI102 | System Meter Phase B Voltage is Too High | 1 | Normal | Alarm | SYS.MMXU.PhV.phsB.range.max |  | Alarm | M
BI103 | System Meter Phase B Voltage is Too Low | 1 | Normal | Alarm | SYS.MMXU.PhV.phsB.range.min |  | Alarm | M
BI104 | System Meter Phase C Voltage is Too High | 1 | Normal | Alarm | SYS.MMXU.PhV.phsC.range.max |  | Alarm | M
BI105 | System Meter Phase C Voltage is Too Low | 1 | Normal | Alarm | SYS.MMXU.PhV.phsC.range.min |  | Alarm | M
BI106 | System Meter Communication Error | 1 | Normal: No Active Communications Error | Alarm: Active Communications Error | LCCH2.ChLiv |  | Alarm | M
BI107 | Selected Curve is Referenced by a Mode | 1 | Curve is not Referenced | Curve is Referenced | MESA.CrvRef |  | Curve | M
BI110 | Renewables only charging status | 2 | Disabled | Enabled | DREN.Mod | BO43 | Renewable energy charging | C: For Function
BI112 | Operating Mode - Frequency-Watt Droop Function. Using Watts per Hz | 2 | Percent | Watts | DHFW3.Mod | BO44 | Droop Freq-Watt | C: For Function | M as watts
BI113 | Type of Active Power Limit. Use Percent or Watts | 2 | Percent | Watts | DWMX1.Mod | BO45 | Active Power Limit | C: For Function
BI114 | Type of Charge/Discharge Target. Use percent or watts | 2 | Percent | Watts | DWGCX1.Mod | BO46 | Charge/Discharge | C: For Function
BI115 | Constant Vars. Use percent or vars | 2 | Percent | Vars | DVAR1.Mod | BO47 | Constant Vars | C: For Function | M as vars
BI2000 | Selected Schedule is Ready | 2 | Not Validated | Validated | BC.FSCHn.SchdSt.2 | BO2000 | BC Scheduling | C: For BC Scheduling
BI2001 | Selected Schedule Repeat Weekly Sunday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.1 | BO2001 | BC Scheduling | C: For BC Scheduling
BI2002 | Selected Schedule Repeat Weekly Monday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.2 | BO2002 | BC Scheduling | C: For BC Scheduling
BI2003 | Selected Schedule Repeat Weekly Tuesday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.3 | BO2003 | BC Scheduling | C: For BC Scheduling
BI2004 | Selected Schedule Repeat Weekly Wednesday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.4 | BO2004 | BC Scheduling | C: For BC Scheduling
BI2005 | Selected Schedule Repeat Weekly Thursday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.5 | BO2005 | BC Scheduling | C: For BC Scheduling
BI2006 | Selected Schedule Repeat Weekly Friday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.6 | BO2006 | BC Scheduling | C: For BC Scheduling
BI2007 | Selected Schedule Repeat Weekly Saturday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.7 | BO2007 | BC Scheduling | C: For BC Scheduling
BI3000 | Selected Schedule is Validated by Outstation | 2 | Not Validated | Validated | FSCHn.SchdSt.2 | BO3000 | Scheduling | C: For 1815.2 Scheduling
BI3001 | Selected Schedule Is Enabled by Controlling Station | 2 | Disabled | Enabled | FSCHn.SchdSt.3 | BO3001 | Scheduling | C: For 1815.2 Scheduling
BI3002 | Selected Schedule Repeat Weekly Sunday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.1 | BO3002 | Scheduling | C: For 1815.2 Scheduling
BI3003 | Selected Schedule Repeat Weekly Monday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.2 | BO3003 | Scheduling | C: For 1815.2 Scheduling
BI3004 | Selected Schedule Repeat Weekly Tuesday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.3 | BO3004 | Scheduling | C: For 1815.2 Scheduling
BI3005 | Selected Schedule Repeat Weekly Wednesday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.4 | BO3005 | Scheduling | C: For 1815.2 Scheduling
BI3006 | Selected Schedule Repeat Weekly Thursday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.5 | BO3006 | Scheduling | C: For 1815.2 Scheduling
BI3007 | Selected Schedule Repeat Weekly Friday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.6 | BO3007 | Scheduling | C: For 1815.2 Scheduling
BI3008 | Selected Schedule Repeat Weekly Saturday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.7 | BO3008 | Scheduling | C: For 1815.2 Scheduling
BI5000 | Active Power at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotW.range |  | Equipment Data
BI5001 | Active Power at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotW.range |  | Equipment Data
BI5002 | Reactive Power at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotVAr.range |  | Equipment Data
BI5003 | Reactive Power at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotVAr.range |  | Equipment Data
BI5004 | Power Factor at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotPF.range |  | Equipment Data
BI5005 | Power Factor at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotPF.range |  | Equipment Data
BI5006 | Phase A Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsA.range |  | Equipment Data
BI5007 | Phase A Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsA.range |  | Equipment Data
BI5008 | Phase B Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsB.range |  | Equipment Data
BI5009 | Phase B Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsB.range |  | Equipment Data
BI5010 | Phase C Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsC.range |  | Equipment Data
BI5011 | Phase C Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsC.range |  | Equipment Data
BI5012 | Meter #1 Communication Error | 1 | Normal: No Active Communications Error | Alarm: Active Communications Error | Meter1.LCCH.ChLiv |  | Equipment Data
BI10000 | DER Unit #1 Is In Maintenance Operational State | 1 | Not in Maintenance | In Maintenance | DER_Unit1.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI10001 | DER Unit #1 Has P1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | DER_Unit1.CALH.GrAlm |  | Equipment Data
BI10002 | DER Unit #1 Has P2 Alarms | 1 | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | DER_Unit1.CALH.GrWrn |  | Equipment Data
BI10003 | DER Unit #1 Has P3 Alarms | 1 | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | DER_Unit1.CALH.GrInd |  | Equipment Data
BI15000 | Inverter #1 Active Power Output is Too High | 1 | Normal | Alarm | Inverter1.MMXU.TotW.range |  | Equipment Data
BI15001 | Inverter #1 Active Power Output is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.TotW.range |  | Equipment Data
BI15002 | Inverter #1 Reactive Power Output is Too High | 1 | Normal | Alarm | Inverter1.MMXU.TotVAr.range |  | Equipment Data
BI15003 | Inverter #1 Reactive Power Output is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.TotVAr.range |  | Equipment Data
BI15004 | Inverter #1 Current Output Frequency is Too High | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15005 | Inverter #1 Current Output Frequency is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15006 | Inverter #1 DC Input Power is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Watt.range |  | Equipment Data
BI15007 | Inverter #1 DC Input Power is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Watt.range |  | Equipment Data
BI15008 | Inverter #1 DC Current Level is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Amp.range |  | Equipment Data
BI15009 | Inverter #1 DC Current Level is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Amp.range |  | Equipment Data
BI15010 | Inverter #1 DC Input Voltage is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15011 | Inverter #1 DC Input Voltage is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15012 | Inverter #1 DNP3 Power Factor Excitation. Operating quadrant of the inverter. | 1 | Overexcited (producing VARs - Q1/Q2) | Underexcited (absorbing VARs - Q3/Q4) | Inverter1.DSTO.PFExtSet |  | Equipment Data
BI15013 | Inverter #1 Communication Error | 1 | Normal | Alarm | Inverter1.LCCH.ChLiv |  | Equipment Data
BI15014 | Inverter #1 Is In Local Control Mode | 1 | Normal | Alarm | Inverter1.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI15015 | Inverter #1 Is DC Contactor Closed | 1 | Normal | Alarm | Inverter1.DINV.InvSwiAlm |  | Equipment Data
BI15016 | Inverter #1 Ground Fault Alarm | 1 | Normal | Alarm | Inverter1.PDIS.Str |  | Equipment Data
BI15017 | Inverter #1 DC Over Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15018 | Inverter #1 DC Under Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15019 | Inverter #1 AC Disconnect Warning | 1 | Normal | Alarm | Inverter1.DINV.InvACLosAlm |  | Equipment Data
BI15020 | Inverter #1 DC Disconnect Warning | 1 | Normal | Alarm | Inverter1.DINV.InvDCLosAlm |  | Equipment Data
BI15021 | Inverter #1 Grid Disconnect Warning | 1 | Normal | Inverter does not detect power on the grid | Inverter1.DINV.InvGriLosAlm |  | Equipment Data
BI15022 | Inverter #1 Cabinet Open Warning | 1 | Normal | Alarm | Inverter1.SPSE.GteSt.open |  | Equipment Data
BI15023 | Inverter #1 Manual Shutdown Warning | 1 | Normal | Alarm | Inverter1.DINV.InvManStopSt |  | Equipment Data
BI15024 | Inverter #1 Over Temperature Alarm | 1 | Normal | Alarm | Inverter1.DINV.EnclTmp.range |  | Equipment Data
BI15025 | Inverter #1 Under Temperature Alarm | 1 | Normal | Alarm | Inverter1.DINV.EnclTmp.range |  | Equipment Data
BI15026 | Inverter #1 Over Frequency Alarm | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15027 | Inverter #1 Under Frequency Alarm | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15028 | Inverter #1 AC Over Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMXU.PhV.PhsA.range |  | Equipment Data
BI15029 | Inverter #1 AC Under Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMXU.PhV.PhsA.range |  | Equipment Data
BI15030 | Inverter #1 Blown String Fuse Alarm | 1 | Normal | Alarm | Inverter1.XFUS.FuSt |  | Equipment Data
BI15031 | Inverter #1 Memory Loss Alarm | 1 | Normal | Alarm | Inverter1.MESA.MemLosAlm |  | Equipment Data
BI15032 | Inverter #1 Hardware Test Failure | 1 | Normal | Alarm | Inverter1.DINV.TestRsl |  | Equipment Data
BI15033 | Inverter #1 Other Alarm | 1 | Normal | Alarm | Inverter1.CALH.GrAlm |  | Equipment Data
BI15034 | Inverter #1 Other Warning | 1 | Normal | Alarm | Inverter1.CALH.GrWrn |  | Equipment Data
BI15070 | Inverter #3 Active Power Output is Too High | 1 | Normal | Alarm | Inverter3.MMXU.TotW.range |  | Equipment Data
BI15071 | Inverter #3 Active Power Output is Too Low | 1 | Normal | Alarm | Inverter3.MMXU.TotW.range |  | Equipment Data
BI15072 | Inverter #3 Reactive Power Output is Too High | 1 | Normal | Alarm | Inverter3.MMXU.TotVAr.range |  | Equipment Data
BI15073 | Inverter #3 Reactive Power Output is Too Low | 1 | Normal | Alarm | Inverter3.MMXU.TotVAr.range |  | Equipment Data
BI15074 | Inverter #3 current Output Frequency is Too High | 1 | Normal | Alarm | Inverter3.MMXU.Hz.range |  | Equipment Data
BI15075 | Inverter #3 current Output Frequency is Too Low | 1 | Normal | Alarm | Inverter3.MMXU.Hz.range |  | Equipment Data
BI15076 | Inverter #3 DC Input Power is Too High | 1 | Normal | Alarm | Inverter3.MMDC.Watt.range |  | Equipment Data
BI15077 | Inverter #3 DC Input Power is Too Low | 1 | Normal | Alarm | Inverter3.MMDC.Watt.range |  | Equipment Data
BI15078 | Inverter #3 DC Current Level is Too High | 1 | Normal | Alarm | Inverter3.MMDC.Amp.range |  | Equipment Data
BI15079 | Inverter #3 DC Current Level is Too Low | 1 | Normal | Alarm | Inverter3.MMDC.Amp.range |  | Equipment Data
BI15080 | Inverter #3 DC Input Voltage is Too High | 1 | Normal | Alarm | Inverter3.MMDC.Vol.range |  | Equipment Data
BI15081 | Inverter #3 DC Input Voltage is Too Low | 1 | Normal | Alarm | Inverter3.MMDC.Vol.range |  | Equipment Data
BI15082 | Inverter #3 DNP3 Power Factor Excitation | 1 | Overexcited (producing VARs - Q1/Q2) | Underexcited (absorbing VARs - Q3/Q4) | Inverter3.DSTO.PFExtSet |  | Equipment Data
BI15083 | Inverter #3 Communication Error | 1 | Normal | Alarm | Inverter3.LCCH.ChLiv |  | Equipment Data
BI15084 | Inverter #3 Is In Local Control Mode | 1 | Normal | Alarm | Inverter3.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI15085 | Inverter #3 Is DC Contactor Closed | 1 | Normal | Alarm | Inverter3.DINV.InvSwiAlm |  | Equipment Data
BI15086 | Inverter #3 Ground Fault Alarm | 1 | Normal | Alarm | Inverter3.PDIS.Str |  | Equipment Data
BI15087 | Inverter #3 DC Over Voltage Alarm | 1 | Normal | Alarm | Inverter3.MMDC.Vol.range |  | Equipment Data
BI15088 | Inverter #3 DC Under Voltage Alarm | 1 | Normal | Alarm | Inverter3.MMDC.Vol.range |  | Equipment Data
BI15089 | Inverter #3 AC Disconnect Warning | 1 | Normal | Alarm | Inverter3.DINV.InvACLosAlm |  | Equipment Data
BI15090 | Inverter #3 DC Disconnect Warning | 1 | Normal | Alarm | Inverter3.DINV.InvDCLosAlm |  | Equipment Data
BI15091 | Inverter #3 Grid Disconnect Warning | 1 | Normal | Inverter does not detect power on the grid | Inverter3.DINV.InvGriLosAlm |  | Equipment Data
BI15092 | Inverter #3 Cabinet Open Warning | 1 | Normal | Alarm | Inverter3.SPSE.GteSt.open |  | Equipment Data
BI15093 | Inverter #3 Manual Shutdown Warning | 1 | Normal | Alarm | Inverter3.DINV.InvManStopSt |  | Equipment Data
BI15094 | Inverter #3 Over Temperature Alarm | 1 | Normal | Alarm | Inverter3.DINV.EnclTmp.range |  | Equipment Data
BI15095 | Inverter #3 Under Temperature Alarm | 1 | Normal | Alarm | Inverter3.DINV.EnclTmp.range |  | Equipment Data
BI15096 | Inverter #3 Over Frequency Alarm | 1 | Normal | Alarm | Inverter3.MMXU.Hz.range |  | Equipment Data
BI15097 | Inverter #3 Under Frequency Alarm | 1 | Normal | Alarm | Inverter3.MMXU.Hz.range |  | Equipment Data
BI15098 | Inverter #3 AC Over Voltage Alarm | 1 | Normal | Alarm | Inverter3.MMXU.PhV.PhsA.range |  | Equipment Data
BI15099 | Inverter #3 AC Under Voltage Alarm | 1 | Normal | Alarm | Inverter3.MMXU.PhV.PhsA.range |  | Equipment Data
BI15100 | Inverter #3 Blown String Fuse Alarm | 1 | Normal | Alarm | Inverter3.XFUS.FuSt |  | Equipment Data
BI15101 | Inverter #3 Memory Loss Alarm | 1 | Normal | Alarm | Inverter3.MESA.MemLosAlm |  | Equipment Data
BI15102 | Inverter #3 Hardware Test Failure | 1 | Normal | Alarm | Inverter3.DINV.TestRsl |  | Equipment Data
BI15103 | Inverter #3 Other Alarm | 1 | Normal | Alarm | Inverter3.CALH.GrAlm |  | Equipment Data
BI15104 | Inverter #3 Other Warning | 1 | Normal | Alarm | Inverter3.CALH.GrWrn |  | Equipment Data
BI20000 | Battery Bank #1 Status of Storage | 3 | Dis-connected | Connected | Battery1.DBAT.BatSt.connected |  | Equipment Data
BI20001 | Battery Bank #1 Communication Error | 1 | Normal | Alarm | Battery1.LCCH.ChLiv |  | Equipment Data
BI20002 | Battery Bank #1 Is In Local Control Mode | 1 | Not in Local Control | In Local Control | Battery1.DBAT.BatSt.localcontrol |  | Equipment Data
BI20003 | Battery Bank #1 Is DC Contactor Closed | 1 | Not Closed | Closed | Battery1.DBAT.DCSwCls |  | Equipment Data
BI20004 | Battery Bank #1 Is Charging | 1 | Not Charging | Charging | Battery1.DBAT.ChaSt |  | Equipment Data
BI20005 | Battery Bank #1 Is Discharging | 1 | Not Discharging | Discharging | Battery1.DBAT.DschSt |  | Equipment Data
BI20006 | Battery Bank #1 External Voltage is Too High | 1 | Normal | Alarm | Battery1.DBAT.ExtVolHiAlm |  | Equipment Data
BI20007 | Battery Bank #1 External Voltage is Too Low | 1 | Normal | Alarm | Battery1.DBAT.ExtVolLoAlm |  | Equipment Data
BI20008 | Battery Bank #1 Internal Voltage is Too High | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiAlm |  | Equipment Data
BI20009 | Battery Bank #1 Internal Voltage is Too Low | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoAlm |  | Equipment Data
BI20010 | Battery Bank #1 Over Temperature Alarm | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpHiAlm |  | Equipment Data
BI20011 | Battery Bank #1 Under Temperature Alarm | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpLoAlm |  | Equipment Data
BI20012 | Battery Bank #1 Temperature Imbalance Alarm | 1 | Normal | Alarm | Battery1.DBAT.UnbTmpAlm |  | Equipment Data
BI20013 | Battery Bank #1 Over Temperature Warning | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpHiWrn |  | Equipment Data
BI20014 | Battery Bank #1 Under Temperature Warning | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpLoWrn |  | Equipment Data
BI20015 | Battery Bank #1 Temperature Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbTmpWrn |  | Equipment Data
BI20016 | Battery Bank #1 Over Charge Current Alarm | 1 | Normal | Alarm | Battery1.DBAT.ChaAmpHiAlm |  | Equipment Data
BI20017 | Battery Bank #1 Over Discharge Current Alarm | 1 | Normal | Alarm | Battery1.DBAT.DschAmpHiAlm |  | Equipment Data
BI20018 | Battery Bank #1 Over Charge Current Warning | 1 | Normal | Alarm | Battery1.DBAT.ChaAmpHiWrn |  | Equipment Data
BI20019 | Battery Bank #1 Over Discharge Current Warning | 1 | Normal | Alarm | Battery1.DBAT.DschAmpHiWrn |  | Equipment Data
BI20020 | Battery Bank #1 Voltage Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbVolWrn |  | Equipment Data
BI20021 | Battery Bank #1 Current Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbAmpWrn |  | Equipment Data
BI20022 | Battery Bank #1 Over Voltage Alarm | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiAlm |  | Equipment Data
BI20023 | Battery Bank #1 Under Voltage Alarm | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoAlm |  | Equipment Data
BI20024 | Battery Bank #1 Over Voltage Warning | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiWrn |  | Equipment Data
BI20025 | Battery Bank #1 Under Voltage Warning | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoWrn |  | Equipment Data
BI20026 | Battery Bank #1 Over State of Charge Maximum Alarm | 1 | Normal | Alarm | Battery1.DBAT.SocHiAlm |  | Equipment Data
BI20027 | Battery Bank #1 Under State of Charge Minimum Alarm | 1 | Normal | Alarm | Battery1.DBAT.SocLoAlm |  | Equipment Data
BI20028 | Battery Bank #1 Over State of Charge Maximum Warning | 1 | Normal | Alarm | Battery1.DBAT.SocHiWrn |  | Equipment Data
BI20029 | Battery Bank #1 Under State of Charge Minimum Warning | 1 | Normal | Alarm | Battery1.DBAT.SocLoWrn |  | Equipment Data
BI20030 | Battery Bank #1 Contactor Failure | 1 | Normal | Alarm | Battery1.MESA.ContFail |  | Equipment Data
BI20031 | Battery Bank #1 Fan Error | 1 | Normal | Alarm | Battery1.MESA.FanErr |  | Equipment Data
BI20032 | Battery Bank #1 Ground Fault | 1 | Normal | Alarm | Battery1.MESA.GndFlt |  | Equipment Data
BI20033 | Battery Bank #1 Door Open Alarm | 1 | Normal | Alarm | Battery1.MESA.DoorOpnAlm |  | Equipment Data
BI20034 | Battery Bank #1 Configuration Error | 1 | Normal | Alarm | Battery1.MESA.ConfErr |  | Equipment Data
BI20035 | Battery Bank #1 Configuration Warning | 1 | Normal | Alarm | Battery1.MESA.ConfWrn |  | Equipment Data
BI20036 | Battery Bank #1 Other Alarm | 1 | Normal | Alarm | Battery1.MESA.OthAlm |  | Equipment Data
BI20037 | Battery Bank #1 Other Warning | 1 | Normal | Alarm | Battery1.MESA.OthWrn |  | Equipment Data
BI20038 | Battery Bank #1 Fire Alarm | 1 | Normal | Alarm | Battery1.SFIR.FireAlm |  | Equipment Data
BI20039 | Battery Bank #1 Fire Supervisory Warning | 1 | Normal | Alarm | Battery1.MESA.FireSupWrn |  | Equipment Data
BI20040 | Battery Bank #1 Fire Trouble Warning | 1 | Normal | Alarm | Battery1.MESA.FireWrn |  | Equipment Data
BI20041 | Battery Bank #1 Fire Power Fault Warning | 1 | Normal | Alarm | Battery1.MESA.FireFltWrn |  | Equipment Data
BI20042 | Battery Bank #1 Chiller Alarm | 1 | Normal | Alarm | Battery1.MESA.ClAlm |  | Equipment Data
BI20043 | Battery Bank #1 Chiller Warning | 1 | Normal | Alarm | Battery1.MESA.ClWrn |  | Equipment Data
BI20044 | Battery Bank #1 Air Handler Alarm | 1 | Normal | Alarm | Battery1.MESA.AirCtlAlm |  | Equipment Data
BI20045 | Battery Bank #1 Air Handler Warning | 1 | Normal | Alarm | Battery1.MESA.AirCtlWrn |  | Equipment Data
BI20046 | Battery Bank #1 Fluid Alarm | 1 | Normal | Alarm | Battery1.MESA.FluAlm |  | Equipment Data
BI20047 | Battery Bank #1 Fluid Warning | 1 | Normal | Alarm | Battery1.MESA.FluWrn |  | Equipment Data
BI20048 | Battery Bank #1 Gas Alarm | 1 | Normal | Alarm | Battery1.MESA.GasAlm |  | Equipment Data
BI20049 | Battery Bank #1 Gas Warning | 1 | Normal | Alarm | Battery1.MESA.GasWrn |  | Equipment Data
BI20050 | Battery Bank #1 Electrolyte Alarm | 1 | Normal | Alarm | Battery1.MESA.ElcytAlm |  | Equipment Data
BI20051 | Battery Bank #1 Electrolyte Warning | 1 | Normal | Alarm | Battery1.MESA.ElcytWrn |  | Equipment Data
BI20052 | Battery Bank #1 Electrical Alarm | 1 | Normal | Alarm | Battery1.MESA.ElcAlm |  | Equipment Data
BI20053 | Battery Bank #1 Electrical Warning | 1 | Normal | Alarm | Battery1.MESA.ElcWrn |  | Equipment Data
BI20108 | Battery Bank #3 Status of Storage | 3 | Off | On | Battery3.DBAT.BatSt.connected |  | Equipment Data
BI20109 | Battery Bank #3 Communication Error | 1 | Normal | Alarm | Battery3.LCCH.ChLiv |  | Equipment Data
BI20110 | Battery Bank #3 Is In Local Control Mode | 1 | Not in Local Control | In Local Control | Battery3.DBAT.BatSt.localcontrol |  | Equipment Data
BI20111 | Battery Bank #3 Is DC Contactor Closed | 1 | Not Closed | Closed | Battery3.DBAT.DCSwCls |  | Equipment Data
BI20112 | Battery Bank #3 Is Charging | 1 | Not Charging | Charging | Battery3.DBAT.ChaSt |  | Equipment Data
BI20113 | Battery Bank #3 Is Discharging | 1 | Not Discharging | Discharging | Battery3.DBAT.DschSt |  | Equipment Data
BI20114 | Battery Bank #3 External Voltage is Too High | 1 | Normal | Alarm | Battery3.DBAT.ExtVolHiAlm |  | Equipment Data
BI20115 | Battery Bank #3 External Voltage is Too Low | 1 | Normal | Alarm | Battery3.DBAT.ExtVolLoAlm |  | Equipment Data
BI20116 | Battery Bank #3 Internal Voltage is Too High | 1 | Normal | Alarm | Battery3.DBAT.IntnVolHiAlm |  | Equipment Data
BI20117 | Battery Bank #3 Internal Voltage is Too Low | 1 | Normal | Alarm | Battery3.DBAT.IntnVolLoAlm |  | Equipment Data
BI20118 | Battery Bank #3 Over Temperature Alarm | 1 | Normal | Alarm | Battery3.DBAT.ExtTmpHiAlm |  | Equipment Data
BI20119 | Battery Bank #3 Under Temperature Alarm | 1 | Normal | Alarm | Battery3.DBAT.ExtTmpLoAlm |  | Equipment Data
BI20120 | Battery Bank #3 Temperature Imbalance Alarm | 1 | Normal | Alarm | Battery3.DBAT.UnbTmpAlm |  | Equipment Data
BI20121 | Battery Bank #3 Over Temperature Warning | 1 | Normal | Alarm | Battery3.DBAT.ExtTmpHiWrn |  | Equipment Data
BI20122 | Battery Bank #3 Under Temperature Warning | 1 | Normal | Alarm | Battery3.DBAT.ExtTmpLoWrn |  | Equipment Data
BI20123 | Battery Bank #3 Temperature Imbalance Warning | 1 | Normal | Alarm | Battery3.DBAT.UnbTmpWrn |  | Equipment Data
BI20124 | Battery Bank #3 Over Charge Current Alarm | 1 | Normal | Alarm | Battery3.DBAT.ChaAmpHiAlm |  | Equipment Data
BI20125 | Battery Bank #3 Over Discharge Current Alarm | 1 | Normal | Alarm | Battery3.DBAT.DschAmpHiAlm |  | Equipment Data
BI20126 | Battery Bank #3 Over Charge Current Warning | 1 | Normal | Alarm | Battery3.DBAT.ChaAmpHiWrn |  | Equipment Data
BI20127 | Battery Bank #3 Over Discharge Current Warning | 1 | Normal | Alarm | Battery3.DBAT.DschAmpHiWrn |  | Equipment Data
BI20128 | Battery Bank #3 Voltage Imbalance Warning | 1 | Normal | Alarm | Battery3.DBAT.UnbVolWrn |  | Equipment Data
BI20129 | Battery Bank #3 Current Imbalance Warning | 1 | Normal | Alarm | Battery3.DBAT.UnbAmpWrn |  | Equipment Data
BI20130 | Battery Bank #3 Over Voltage Alarm | 1 | Normal | Alarm | Battery3.DBAT.IntnVolHiAlm |  | Equipment Data
BI20131 | Battery Bank #3 Under Voltage Alarm | 1 | Normal | Alarm | Battery3.DBAT.IntnVolLoAlm |  | Equipment Data
BI20132 | Battery Bank #3 Over Voltage Warning | 1 | Normal | Alarm | Battery3.DBAT.IntnVolHiWrn |  | Equipment Data
BI20133 | Battery Bank #3 Under Voltage Warning | 1 | Normal | Alarm | Battery3.DBAT.IntnVolLoWrn |  | Equipment Data
BI20134 | Battery Bank #3 Over State of Charge Maximum Alarm | 1 | Normal | Alarm | Battery3.DBAT.SocHiAlm |  | Equipment Data
BI20135 | Battery Bank #3 Under State of Charge Minimum Alarm | 1 | Normal | Alarm | Battery3.DBAT.SocLoAlm |  | Equipment Data
BI20136 | Battery Bank #3 Over State of Charge Maximum Warning | 1 | Normal | Alarm | Battery3.DBAT.SocHiWrn |  | Equipment Data
BI20137 | Battery Bank #3 Under State of Charge Minimum Warning | 1 | Normal | Alarm | Battery3.DBAT.SocLoWrn |  | Equipment Data
BI20138 | Battery Bank #3 Contactor Failure | 1 | Normal | Alarm | Battery3.MESA.ContFail |  | Equipment Data
BI20139 | Battery Bank #3 Fan Error | 1 | Normal | Alarm | Battery3.MESA.FanErr |  | Equipment Data
BI20140 | Battery Bank #3 Ground Fault | 1 | Normal | Alarm | Battery3.MESA.GndFlt |  | Equipment Data
BI20141 | Battery Bank #3 Door Open Alarm | 1 | Normal | Alarm | Battery3.MESA.DoorOpnAlm |  | Equipment Data
BI20142 | Battery Bank #3 Configuration Error | 1 | Normal | Alarm | Battery3.MESA.ConfErr |  | Equipment Data
BI20143 | Battery Bank #3 Configuration Warning | 1 | Normal | Alarm | Battery3.MESA.ConfWrn |  | Equipment Data
BI20144 | Battery Bank #3 Other Alarm | 1 | Normal | Alarm | Battery3.MESA.OthAlm |  | Equipment Data
BI20145 | Battery Bank #3 Other Warning | 1 | Normal | Alarm | Battery3.MESA.OthWrn |  | Equipment Data
BI20146 | Battery Bank #3 Fire Alarm | 1 | Normal | Alarm | Battery3.SFIR.FireAlm |  | Equipment Data
BI20147 | Battery Bank #3 Fire Supervisory Warning | 1 | Normal | Alarm | Battery3.MESA.FireSupWrn |  | Equipment Data
BI20148 | Battery Bank #3 Fire Trouble Warning | 1 | Normal | Alarm | Battery3.MESA.FireWrn |  | Equipment Data
BI20149 | Battery Bank #3 Fire Power Fault Warning | 1 | Normal | Alarm | Battery3.MESA.FireFltWrn |  | Equipment Data
BI20150 | Battery Bank #3 Chiller Alarm | 1 | Normal | Alarm | Battery3.MESA.ClAlm |  | Equipment Data
BI20151 | Battery Bank #3 Chiller Warning | 1 | Normal | Alarm | Battery3.MESA.ClWrn |  | Equipment Data
BI20152 | Battery Bank #3 Air Handler Alarm | 1 | Normal | Alarm | Battery3.MESA.AirCtlAlm |  | Equipment Data
BI20153 | Battery Bank #3 Air Handler Warning | 1 | Normal | Alarm | Battery3.MESA.AirCtlWrn |  | Equipment Data
BI20154 | Battery Bank #3 Fluid Alarm | 1 | Normal | Alarm | Battery3.MESA.FluAlm |  | Equipment Data
BI20155 | Battery Bank #3 Fluid Warning | 1 | Normal | Alarm | Battery3.MESA.FluWrn |  | Equipment Data
BI20156 | Battery Bank #3 Gas Alarm | 1 | Normal | Alarm | Battery3.MESA.GasAlm |  | Equipment Data
BI20157 | Battery Bank #3 Gas Warning | 1 | Normal | Alarm | Battery3.MESA.GasWrn |  | Equipment Data
BI20158 | Battery Bank #3 Electrolyte Alarm | 1 | Normal | Alarm | Battery3.MESA.ElcytAlm |  | Equipment Data
BI20159 | Battery Bank #3 Electrolyte Warning | 1 | Normal | Alarm | Battery3.MESA.ElcytWrn |  | Equipment Data
BI20160 | Battery Bank #3 Electrical Alarm | 1 | Normal | Alarm | Battery3.MESA.ElcAlm |  | Equipment Data
BI20161 | Battery Bank #3 Electrical Warning | 1 | Normal | Alarm | Battery3.MESA.ElcWrn |  | Equipment Data
BI30000 | Supports Volt-Watt Advanced Mode | 0 | Not Supported | Supported | DVWC1 |  | Volt-Watt Advanced
BI30001 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWC1.Mod | BO30000 | Volt-Watt Advanced | C: For Function
BI30010 | Supports Synthetic Inertia Function | 0 | Not Supported | Supported | DSYN |  | Synthetic Inertia | C: For Function
BI30011 | Operating Mode - Synthetic Inertia Enabled | 2 | Disabled | Enabled | DSYN.Mod | BO30010 | Synthetic Inertia | C: For Function
VP | Vendor Points

## AO
DNP3 Point Index | Name / Description | Transmitted Value |  | Scaling |  | Units | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  | Minimum | Maximum | Multiplier | OffSet |  | IEC61850UniqueString | Assoc. AI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AO0 | Reference Voltage | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VRef | AI29 | Config
AO1 | Reference Voltage Offset | -2147483648 | 2147483647 | 0.1 | 0 | Volts | DECP.VRefOfs | AI30 | Config
AO2 | Nominal Grid Frequency | 0 | 70000 | 0.001 | 0 | Hz | DECP.EcpHzNom | AI31 | Config
AO3 | Open Loop Response Time Percentage. Percent of target to reach within the open loop response time. Default is 90%. | 0 | 1000 | 0.1 | 0 | Percent | DGEN.OplPct |  | Operational Settings
AO4 | Power Factor Sign Convention. <1> IEC – active power <2> IEEE – lead/lag | 1 | 2 | 1 | 0 | None | MMXU1.PFSign | AI41 | Operational Settings
AO5 | Reference for Reactive Power Setpoints. Selects which setpoint is active. Default is <3>. <0> Not applicable / Unknown <1> Percent of Maximum Active Power (WMax) <2> Percent of Maximum Reactive Power (VArMax) <3> Percent of Available Reactive Power (VArAval) | 0 | 3 | 1 | 0 | Enum | DGEN.VArRef | AI42 | Operational Settings
AO6 | DER Start (Return to Service) Voltage High Limit. Percent of Reference Voltage. | 0 | 20000 | 0.01 | 0 | Percent | DCTE1.VHiLim | AI50 | Return to Service
AO7 | DER Start (Return to Service) Voltage Low Limit. Percent of Reference Voltage. | 0 | 10000 | 0.01 | 0 | Percent | DCTE1.VLoLim | AI51 | Return to Service
AO8 | DER Start (Return to Service) Frequency High Limit | 0 | 70000 | 0.001 | 0 | Hz | DCTE1.HzHiLim | AI52 | Return to Service
AO9 | DER Start (Return to Service) Frequency Low Limit | 0 | 70000 | 0.001 | 0 | Hz | DCTE1.HzLoLim | AI53 | Return to Service
AO10 | DER Start (Return to Service) Delay | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.RtnDlyTmms | AI54 | Return to Service
AO11 | DER Start (Return to Service) Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.WinTms | AI55 | Return to Service
AO12 | DER Start (Return to Service) Ramp Up Time | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.RtnRmpTmms | AI56 | Return to Service
AO13 | DER Stop (Cease to Energize)Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.WinTms | AI57 | Cease
AO14 | DER Stop (Cease to Energize) Ramp Down Time | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.RmpTms | AI58 | Cease
AO15 | DER Stop (Cease to Energize) Reversion Timeout Period. Time to revert from the stopped state and return to service. | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.RvrtTms | AI59 | Cease
AO16 | Connect/Disconnect Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DCTE3.WinTms | AI60 | Connect
AO17 | Connect/Disconnect Reversion Timeout Period. Timeout (reversion time is for the Disconnect only) | 0 | 2147483647 | 1 | 0 | Seconds | DCTE3.RvrtTms | AI61 | Connect
AO18 | Requested Island Configuration. Enumeration: <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 0 | 255 | 1 | 0 | Enum | DECP1.EcpIsldSt |  | Operational Settings
AO19 | Islanded Configuration Being Edited. Enumeration: <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 0 | 255 | 1 | 0 | Enum | DECPn.EcpIsldSt |  | Operational Settings
AO20 | Freeze Counter Interval. Interval between freeze counter operations after the initial occurrence. A zero value means the free counter operation is not repeated. | 0 | 2147483647 | 1 | 0 | n/a | MESA.FrzIntv |  | Metering
AO21 | Freeze Counter Interval Units. Units of the interval between freeze counter operations: <0> The outstation does not repeat the action, regardless of the Interval count. <1> Milliseconds - In this case the interval is always counted relative to the Start Time and is constant regardless of the clock time set at the Outstation. <2> Seconds - At the same millisecond within the second that is specified in the Start Time. <3> Minutes - At the same second and millisecond within the minute that is specified in the Start Time. <4> Hours - At the same minute, second and B7millisecond within the hour that is specified in the Start Time. <5> Days - At the same time of day that is specified in the Start Time. <6> Weeks - On the same day of the week at the same time of day that is specified in the Start Time <7> Months - On the same day of each month at the same time of day that is specified in the Start Time. If the Start Time falls on the 29th or greater day of the month, the outstation shall not perform the action in months that do not have such a day <8> Months on Same Day of Week from Start of Month - At the same timeof day on the same day of the week after the beginning of the month as the day specified in the Start Time. For instance, if the Start Time specifies the second Tuesday of February and the Interval Count is 2, the next action shall occur on the second Tuesday of April. In the same example, if the Interval Count is set to 12, this is the same as specifying, “Every year on the second Tuesday in February”. If the specified day does not occur in a given month when an action was scheduled to occur, the outstation shall not perform the action that month but shall perform it at the next valid scheduled time. <9> Months on Same Day of Week from End of Month - The outstation shall interpret this setting as in <8>, but the day of the week shall be measured from the end of the month, e.g.,“the second-last Tuesday in February”. | 0 | 9 | 1 | 0 | Enum | MESA.FrzIntvUnt | AI70 | Metering
AO22 | Low/High Voltage Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.EcpRef | AI71 | Volt Ride-Through | C: For Function, unless set at implementation
AO23 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV1.BlkRef | AI73 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO24 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV1.BlkRef | AI74 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO25 | Low/High Voltage Ride-Through High Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV2.BlkRef | AI75 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO26 | Low/High Voltage Ride-Through Low Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV2.BlkRef | AI76 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO27 | Low/High Frequency Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.EcpRef | AI77 | Freq Ride-Through | C: For Function, unless set at implementation
AO28 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF1.BlkRef | AI79 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO29 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF1.BlkRef | AI80 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO30 | Low/High Frequency Ride-Through High Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation/discharging must stop when the frequency is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF2.BlkRef | AI81 | Freq Ride-Through | C: For Function, unless set at implementation
AO31 | Low/High Frequency Ride-Through Low Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation/discharging must stop when the frequency is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF2.BlkRef | AI82 | Freq Ride-Through | C: For Function, unless set at implementation
AO32 | Dynamic Reactive Current Support Mode Priority | 0 | 100 | 1 | 0 | n/a | DRGS.ModPrio | AI83 | Dyn React Curr Supp
AO33 | Dynamic Reactive Current Support Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.WinTms | AI84 | Dyn React Curr Supp
AO34 | Dynamic Reactive Current Support Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.RmpTms | AI85 | Dyn React Curr Supp
AO35 | Dynamic Reactive Current Support Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.RvrtTms | AI86 | Dyn React Curr Supp
AO36 | Dynamic Reactive Current Support Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DRGS.EcpRef | AI87 | Dyn React Curr Supp | C: For Function, unless set at implementation
AO37 | Dynamic Reactive Current Support - Gradient Mode. Enumeration: <0> Undefined <1> Gradients reach 0 at the moving average Voltage <2> Gradients reach 0 at the Voltage deadbands | 0 | 2 | 1 | 0 | Enum | DRGS.ArGraMod | AI91 | Dyn React Curr Supp | C: For Function
AO38 | Dynamic Reactive Current Support Deadband Minimum Voltage. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays above this value for the length of the Hold Time. | -10000 | 0 | 0.1 | 0 | Percent | DRGS.DbVMin | AI92 | Dyn React Curr Supp | C: For Function
AO39 | Dynamic Reactive Current Support Deadband Maximum Voltage. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays below this value for the length of the Hold Time. | 0 | 10000 | 0.1 | 0 | Percent | DRGS.DbVMax | AI93 | Dyn React Curr Supp | C: For Function
AO40 | Dynamic Reactive Current Support Gradient for Sags. Percentage of the rated current (DRAT.ARtg) to apply capacitively per percentage of the negative deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSag | AI94 | Dyn React Curr Supp | C: For Function
AO41 | Dynamic Reactive Current Support Gradient for Swells. Percentage of the rated current (DRAT.ARtg) to apply inductively per percentage of the positive deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSwl | AI95 | Dyn React Curr Supp | C: For Function
AO42 | Dynamic Reactive Current Support Filter Time for Moving Average Voltage (RDGS.VAv). Used to determine amount of dynamic reactive current support. | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.FilTms | AI96 | Dyn React Curr Supp | C: For Function
AO43 | Dynamic Reactive Current Support Block Zone Voltage. Percentage of the nominal voltage (DRCT.VRef) below which no reactive current support shall be applied. | 0 | 1000 | 0.1 | 0 | Percent | DRGS.BlkZnV | AI97 | Dyn React Curr Supp | C: For Function
AO44 | Dynamic Reactive Current Support Hysteresis Block Zone Voltage. Percentage of the nominal voltage (DRCT.VRef). After being blocked, reactive current support shall not resume until the voltage has been above BlkZnV + HysBlkZnV. | 0 | 1000 | 0.1 | 0 | Percent | DRGS.HysBlkZnV | AI98 | Dyn React Curr Supp | C: For Function
AO45 | Dynamic Reactive Current Support Block Zone Time. Time in milliseconds from the beginning of any "sag" event, before which dynamic reactive current support will always continue, regardless of how low voltage may sag. | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.BlkZnTmms | AI99 | Dyn React Curr Supp | C: For Function
AO46 | Dynamic Reactive Current Support Start Hold Time. When the voltage exceeds the deadband limits for this length of time (measured in milliseconds), the "sag" or "swell" event begins and the DER may begin altering active power output. | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.HoldTmms | AI100 | Dyn React Curr Supp | C: For Function
AO47 | Dynamic Reactive Current Support End Hold Time. When the voltage returns to within the deadband limits for this length of time (measured in milliseconds), the "sag" or "swell" event is considered to be over. Reactive current support ends, frozen values are unfrozen, and a new event can begin. | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.HoldTmms.1 | AI101 | Dyn React Curr Supp | C: For Function
AO48 | Dynamic Volt-Watt Mode Priority | 0 | 100 | 1 | 0 | n/a | DVWD.ModPrio | AI102 | Dyn Volt-Watt
AO49 | Dynamic Volt-Watt Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.WinTms | AI103 | Dyn Volt-Watt
AO50 | Dynamic Volt-Watt Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.RmpTms | AI104 | Dyn Volt-Watt
AO51 | Dynamic Volt-Watt Reversion Timeout period | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.RvrtTms | AI105 | Dyn Volt-Watt
AO52 | Dynamic Volt-Watt Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVWD2.EcpRef | AI106 | Dyn Volt-Watt | C: For Function, unless set at implementation
AO53 | Dynamic Volt-Watt Gradient. Signed unit-less quantity that establishes the ratio of additional Watts supplied (expressed in terms of % DRCT.WMax) to the present difference from the moving average voltage (expressed as % DRCT.VRef). | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent voltage difference | DVWD.DynVWGra | AI110 | Dyn Volt-Watt | C: For Function
AO54 | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.VWFilTms | AI111 | Dyn Volt-Watt | C: For Function
AO55 | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage (DRCT.Vref) measured below the moving average voltage. If the present voltage is above this value, no additional Watts shall be supplied. | 0 | 1000 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWLo | AI112 | Dyn Volt-Watt | C: For Function
AO56 | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage (DRCT.Vref) measured above the moving average voltage. If the present voltage is below this value, no additional Watts shall be supplied. | 0 | 1000 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWHi | AI113 | Dyn Volt-Watt | C: For Function
AO57 | Frequency-Watt Mode Priority | 0 | 100 | 1 | 0 | n/a | DHFW1.ModPrio | AI115 | Freq-Watt
AO58 | Frequency-Watt Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.WinTms | AI116 | Freq-Watt
AO59 | Frequency-Watt Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.RmpTms | AI117 | Freq-Watt
AO60 | Frequency-Watt Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.RvrtTms | AI118 | Freq-Watt
AO61 | Frequency-Watt Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DHFW1.EcpRef | AI119 | Freq-Watt | C: For Function, unless set at implementation
AO62 | Frequency-Watt High Starting Frequency | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | AI121 | Freq-Watt | C: For Function | M
AO63 | Frequency-Watt High Stopping Frequency | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStop | AI122 | Freq-Watt
AO64 | Frequency-Watt High Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | AI123 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO476 | M
AO65 | Frequency-Watt High Charging Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent frequency difference | DHFW1.WChaGra | AI124 | Freq-Watt
AO66 | Frequency-Watt Low Starting Frequency | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | AI125 | Freq-Watt | C: For Function | M
AO67 | Frequency-Watt Low Stopping Frequency | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStop | AI126 | Freq-Watt
AO68 | Frequency-Watt Low Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | AI127 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO477 | M
AO69 | Frequency-Watt Low Charging Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent frequency difference | DLFW1.WChaGra | AI128 | Freq-Watt
AO70 | Frequency-Watt Start Delay | 0 | 2147483647 | 1 | 0 | ms | DHFW1.ActStrDlTmms | AI129 | Freq-Watt
AO71 | Frequency-Watt Stop Delay | 0 | 2147483647 | 1 | 0 | ms | DHFW1.ActStopDlTmms | AI130 | Freq-Watt
AO72 | Frequency-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.1 | AI131 | Freq-Watt |  | M
AO73 | Frequency-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | AI132 | Freq-Watt |  | M
AO74 | Frequency-Watt Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.DschRpuRte | AI133 | Freq-Watt
AO75 | Frequency-Watt Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.DschRpdRte | AI134 | Freq-Watt
AO76 | Frequency-Watt Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.ChaRpuRte | AI135 | Freq-Watt
AO77 | Frequency-Watt Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.ChaRpdRte | AI136 | Freq-Watt
AO78 | Frequency-Watt High Return Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.RtnRmpRte | AI137 | Freq-Watt
AO79 | Frequency-Watt Low Return Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.RtnRmpRte | AI138 | Freq-Watt
AO80 | Frequency-Watt Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DHFW1.SocUseMin | AI140 | Freq-Watt
AO81 | Frequency-Watt Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DHFW1.SocUseMax | AI141 | Freq-Watt
AO82 | Active Power Limit Mode Priority | 0 | 100 | 1 | 0 | n/a | DWMX.ModPrio | AI142 | Active Power Limit
AO83 | Active Power Limit Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWMX.WinTms | AI143 | Active Power Limit
AO84 | Active Power Limit Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWMX.RmpTms | AI144 | Active Power Limit
AO85 | Active Power Limit Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWMX.RvrtTms | AI145 | Active Power Limit
AO86 | Active Power Limit Signal Meter ID. (POC, PCC, or Other) | 0 | 2147483647 | 1 | 0 | n/a | DWMX.EcpRef | AI146 | Active Power Limit | C: For Function, unless set at implementation
AO87 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | AI148 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO478 | M
AO88 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | AI149 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO479 | M
AO89 | Charge/Discharge Mode Priority | 0 | 100 | 1 | 0 | n/a | DWGC.ModPrio | AI150 | Set Active Power
AO90 | Charge/Discharge Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.WinTms | AI151 | Set Active Power
AO91 | Charge/Discharge Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.RmpTms | AI152 | Set Active Power
AO92 | Charge/Discharge Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.RvrtTms | AI153 | Set Active Power
AO93 | Charge/Discharge Active Power Target | -1000 | 1000 | 0.1 | 0 | Percent of WMax | DWGC.GnWPctSpt | AI154 | Set Active Power | C: For Function
AO94 | Charge/Discharge Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.1 | AI155 | Set Active Power | C: For Function
AO95 | Charge/Discharge Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.2 | AI156 | Set Active Power | C: For Function
AO96 | Charge/Discharge Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.DschRpuRte | AI157 | Set Active Power | C: For Function
AO97 | Charge/Discharge Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.DschRpdRte | AI158 | Set Active Power | C: For Function
AO98 | Charge/Discharge Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.ChaRpuRte | AI159 | Set Active Power | C: For Function
AO99 | Charge/Discharge Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.ChaRpdRte | AI160 | Set Active Power | C: For Function
AO100 | Charge/Discharge Minimum Reserve for Storage | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMinPct | AI161 | Set Active Power | C: For Function
AO101 | Charge/Discharge Maximum Reserve for Storage | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMaxPct | AI162 | Set Active Power | C: For Function
AO102 | Coordinated Charge/Discharge Mode Priority | 0 | 100 | 1 | 0 | n/a | DTCD.ModPrio | AI163 | Coord Charge-Dischg
AO103 | Coordinated Charge/Discharge Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.WinTms | AI164 | Coord Charge-Dischg
AO104 | Coordinated Charge/Discharge Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.RmpTms | AI165 | Coord Charge-Dischg
AO105 | Coordinated Charge/Discharge Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.RvrtTms | AI166 | Coord Charge-Dischg
AO106 | Coordinated Charge/Discharge Target State of Charge | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DTCD.SocUseTgtPct | AI167 | Coord Charge-Dischg | C: For Function
AO107 | Coordinated Charge/Discharge Target Date | 0 | 2147483647 | 1 | 0 | Days | DTCD.DateTgt.Date | AI168 | Coord Charge-Dischg | C: For Function
AO108 | Coordinated Charge/Discharge Target Time | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.DateTgt.Time | AI169 | Coord Charge-Dischg | C: For Function
AO109 | Coordinated Charge/Discharge Energy Request | 0 | 2147483647 | 1 | 0 | Watt-hours | DTCD.WhReq | AI170 | Coord Charge-Dischg | C: For Function
AO110 | Coordinated Charge/Discharge Minimum Charging Duration | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurTms | AI171 | Coord Charge-Dischg | C: For Function
AO111 | Coordinated Charge/Discharge Date of Reference | 0 | 2147483647 | 1 | 0 | Days | DTCD.SocDate | AI172 | Coord Charge-Dischg | C: For Function
AO112 | Coordinated Charge/Discharge Time of Reference | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.SocDateTms | AI173 | Coord Charge-Dischg | C: For Function
AO113 | Coordinated Charge/Discharge Duration at Maximum Charge Rate | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurMax | AI174 | Coord Charge-Dischg | C: For Function
AO114 | Coordinated Charge/Discharge Duration at Maximum Discharge Rate | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.DschDurMax | AI175 | Coord Charge-Dischg | C: For Function
AO115 | Active Power Following Mode #1 (Peak Power Limiting) Priority | 0 | 100 | 1 | 0 | n/a | DWFL1.ModPrio | AI176 | Peak Power Limiting
AO116 | Active Power Following Mode #1 (Peak Power Limiting) Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWFL1.WinTms | AI177 | Peak Power Limiting
AO117 | Active Power Following Mode #1 (Peak Power Limiting) Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWFL1.RmpTms | AI178 | Peak Power Limiting
AO118 | Active Power Following Mode #1 (Peak Power Limiting) Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWFL1.RvrtTms | AI179 | Peak Power Limiting
AO119 | Active Power Following Mode #1 (Peak Power Limiting) Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWFL1.EcpRef | AI180 | Peak Power Limiting | C: For Function, unless set at implementation
AO120 | Active Power Following Mode #1 (Peak Power Limiting) Power Threshold | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.FolWThr | AI182 | Peak Power Limiting | C: For Function
AO121 | Active Power Following Mode #1 (Peak Power Limiting) Ratio. Percent of the power exceeding the Power Threshold | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL1.FolWPct | AI183 | Peak Power Limiting | C: For Function
AO122 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpuRte | AI184 | Peak Power Limiting | C: For Function
AO123 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpdRte | AI185 | Peak Power Limiting | C: For Function
AO124 | Active Power Following Mode #2 (Load Following) Priority | 0 | 100 | 1 | 0 | n/a | DWFL2.ModPrio | AI187 | Load Following
AO125 | Active Power Following Mode #2 (Load Following) Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWFL2.WinTms | AI188 | Load Following
AO126 | Active Power Following Mode #2 (Load Following) Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWFL2.RmpTms | AI189 | Load Following
AO127 | Active Power Following Mode #2 (Load Following) Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWFL2.RvrtTms | AI190 | Load Following
AO128 | Active Power Following Mode #2 (Load Following) Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWFL2.EcpRef | AI191 | Load Following | C: For Function, unless set at implementation
AO129 | Active Power Following Mode #2 (Load Following) Power Threshold | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.FolWThr | AI193 | Load Following | C: For Function
AO130 | Active Power Following Mode #2 (Load Following) Ratio. Percent of the power exceeding the Power Threshold | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL2.FolWPct | AI194 | Load Following | C: For Function
AO131 | Active Power Following Mode #2 (Load Following) Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpuRte | AI195 | Load Following | C: For Function
AO132 | Active Power Following Mode #2 (Load Following) Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpdRte | AI196 | Load Following | C: For Function
AO133 | Active Power Following Mode #3 (Generation Following) Priority | 0 | 100 | 1 | 0 | n/a | DWFL3.ModPrio | AI198 | Generation Following
AO134 | Active Power Following Mode #3 (Generation Following) Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWFL3.WinTms | AI199 | Generation Following
AO135 | Active Power Following Mode #3 (Generation Following) Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWFL3.RmpTms | AI200 | Generation Following
AO136 | Active Power Following Mode #3 (Generation Following) Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWFL3.RvrtTms | AI201 | Generation Following
AO137 | Active Power Following Mode #3 (Generation Following) Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWFL3.EcpRef | AI202 | Generation Following | C: For Function, unless set at implementation
AO138 | Active Power Following Mode #3 (Generation Following) Power Threshold | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.FolWThr | AI204 | Generation Following | C: For Function
AO139 | Active Power Following Mode #3 (Generation Following) Ratio. Percent of the power exceeding the Power Threshold | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL3.FolWPct | AI205 | Generation Following | C: For Function
AO140 | Active Power Following Mode #3 (Generation Following) Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpuRte | AI206 | Generation Following | C: For Function
AO141 | Active Power Following Mode #3 (Generation Following) Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpdRte | AI207 | Generation Following | C: For Function
AO142 | AGC Mode Priority | 0 | 100 | 1 | 0 | n/a | DAGC.ModPrio | AI209 | AGC
AO143 | AGC Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.WinTms | AI210 | AGC
AO144 | AGC Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RmpTms | AI211 | AGC
AO145 | AGC Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RvrtTms | AI212 | AGC
AO146 | AGC Active Power Target | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WSpt | AI213 | AGC | C: For Function
AO147 | AGC Ramp Time Constant Up Time | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.OplTmsMax.1 | AI214 | AGC | C: For Function
AO148 | AGC Ramp Time Constant Down Time | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.OplTmsMax.2 | AI215 | AGC | C: For Function
AO149 | AGC Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.DschRpuRte | AI216 | AGC | C: For Function
AO150 | AGC Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.DschRpdRte | AI217 | AGC | C: For Function
AO151 | AGC Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.ChaRpuRte | AI218 | AGC | C: For Function
AO152 | AGC Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.ChaRpdRte | AI219 | AGC | C: For Function
AO153 | AGC Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMinPct | AI220 | AGC | C: For Function
AO154 | AGC Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMaxPct | AI221 | AGC | C: For Function
AO155 | Active Power Smoothing Mode Priority | 0 | 100 | 1 | 0 | n/a | DWSM.ModPrio | AI227 | Active Power Smoothing
AO156 | Active Power Smoothing Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.WinTms | AI228 | Active Power Smoothing
AO157 | Active Power Smoothing Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.RmpTms | AI229 | Active Power Smoothing
AO158 | Active Power Smoothing Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.RvrtTms | AI230 | Active Power Smoothing
AO159 | Active Power Smoothing Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWSM.EcpRef | AI231 | Active Power Smoothing | C: For Function, unless set at implementation
AO160 | Active Power Smoothing Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Watts per delta-watt | DWSM.WSmthGra | AI233 | Active Power Smoothing
AO161 | Active Power Smoothing Lower Limit | -2147483648 | 0 | 1 | 0 | Watts | DWSM.WSmthLoLim | AI234 | Active Power Smoothing | C: For Function
AO162 | Active Power Smoothing Upper Limit | 0 | 2147483647 | 1 | 0 | Watts | DWSM.WSmthHiLim | AI235 | Active Power Smoothing | C: For Function
AO163 | Active Power Smoothing Filter Time (Seconds) | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.FilTms | AI236 | Active Power Smoothing | C: For Function
AO164 | Active Power Smoothing Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.DschRpuRte | AI237 | Active Power Smoothing | C: For Function
AO165 | Active Power Smoothing Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.DschRpdRte | AI238 | Active Power Smoothing | C: For Function
AO166 | Active Power Smoothing Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.ChaRpuRte | AI239 | Active Power Smoothing | C: For Function
AO167 | Active Power Smoothing Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.ChaRpdRte | AI240 | Active Power Smoothing | C: For Function
AO168 | Volt-Watt Mode Priority | 0 | 100 | 1 | 0 | n/a | DVWC.ModPrio | AI242 | Volt-Watt
AO169 | Volt-Watt Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.WinTms | AI243 | Volt-Watt
AO170 | Volt-Watt Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.RmpTms | AI244 | Volt-Watt
AO171 | Volt-Watt Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.RvrtTms | AI245 | Volt-Watt
AO172 | Volt-Watt Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVWC.EcpRef | AI246 | Volt-Watt | C: For Function, unless set at implementation
AO173 | Volt-Watt Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVWC.VWCrv | AI248 | Volt-Watt | C: For Function, unless set at implementation as zero | C: See clause 1.7
AO174 | Volt-Watt Filter Time (Seconds) | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.FilTms | AI250 | Volt-Watt | C: For Function
AO175 | Volt-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.1 | AI251 | Volt-Watt | C: For Function | M
AO176 | Volt-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.2 | AI252 | Volt-Watt | C: For Function | M
AO177 | Volt-Watt Discharging Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.DschRpuRte | AI253 | Volt-Watt | C: For Function
AO178 | Volt-Watt Discharging Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.DschRpdRte | AI254 | Volt-Watt | C: For Function
AO179 | Volt-Watt Charging Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.ChaRpuRte | AI255 | Volt-Watt | C: For Function
AO180 | Volt-Watt Charging Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.ChaRpdRte | AI256 | Volt-Watt | C: For Function
AO181 | Frequency-Watt Curve Mode Priority | 0 | 100 | 1 | 0 | n/a | DHFW2.ModPrio | AI257 | Freq-Watt Curve
AO182 | Frequency-Watt Curve Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.WinTms | AI258 | Freq-Watt Curve
AO183 | Frequency-Watt Curve Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.RmpTms | AI259 | Freq-Watt Curve
AO184 | Frequency-Watt Curve Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.RvrtTms | AI260 | Freq-Watt Curve
AO185 | Frequency-Watt Curve Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.EcpRef | AI261 | Freq-Watt Curve | C: For Function, unless set at implementation
AO186 | Frequency-Watt Curve - Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HzWCrv | AI263 | Freq-Watt Curve | C: For Function
AO187 | Frequency-Watt Curve - High Frequency Hysteresis Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HysCrv | AI264 | Freq-Watt Curve | C: For Function
AO188 | Frequency-Watt Curve - Low Frequency Hysteresis Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DLFW2.HysCrv | AI265 | Freq-Watt Curve | C: For Function
AO189 | Frequency-Watt Curve Start Delay | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStrDlTmms | AI266 | Freq-Watt Curve | C: For Function
AO190 | Frequency-Watt Curve Stop Delay | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStopDlTmms | AI267 | Freq-Watt Curve | C: For Function
AO191 | Frequency-Watt Curve Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.1 |  | Freq-Watt Curve | C: For Function
AO192 | Frequency-Watt Curve Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.2 | AI269 | Freq-Watt Curve | C: For Function
AO193 | Frequency-Watt Curve Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuRte | AI270 | Freq-Watt Curve | C: For Function
AO194 | Frequency-Watt Curve Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdRte | AI271 | Freq-Watt Curve | C: For Function
AO195 | Frequency-Watt Curve Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuChaRte | AI272 | Freq-Watt Curve | C: For Function
AO196 | Frequency-Watt Curve Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdChaRte | AI273 | Freq-Watt Curve | C: For Function
AO197 | Frequency-Watt Curve Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMinPct | AI275 | Freq-Watt Curve | C: For Function
AO198 | Frequency-Watt Curve Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMaxPct | AI276 | Freq-Watt Curve | C: For Function
AO199 | Constant Vars Mode Priority | 0 | 100 | 1 | 0 | n/a | DVAR.ModPrio | AI277 | Const Vars
AO200 | Constant Vars Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.WinTms | AI278 | Const Vars
AO201 | Constant VArs Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.RmpTms | AI279 | Const Vars
AO202 | Constant Vars Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.RvrtTms | AI280 | Const Vars
AO203 | Constant Vars Reactive Power Target | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | AI281 | Const Vars | C: For Function | M
AO204 | Constant Vars Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.1 | AI282 | Const Vars | C: For Function
AO205 | Constant Vars Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.2 | AI283 | Const Vars | C: For Function
AO206 | Constant Power Factor Mode Priority | 0 | 100 | 1 | 0 | n/a | DFPF.ModPrio | AI284 | Constant PF
AO207 | Constant Power Factor Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DFPF.WinTms | AI285 | Constant PF
AO208 | Constant Power Factor Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DFPF.RmpTms | AI286 | Constant PF
AO209 | Constant Power Factor Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DFPF.RvrtTms | AI287 | Constant PF
AO210 | Constant Power Factor Setpoint - Generation/Discharging | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | AI288 | Constant PF | C: For Function | M
AO211 | Constant Power Factor Setpoint - Charging | 0 | 100 | 0.01 | 0 | None | DFPF.PFLodTgt | AI289 | Constant PF | C: For Function | M
AO212 | Volt-Var Control Mode Priority | 0 | 100 | 1 | 0 | n/a | DVVR.ModPrio | AI290 | Volt-Var
AO213 | Volt-Var Control Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.WinTms | AI291 | Volt-Var
AO214 | Volt-Var Control Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.RmpTms | AI292 | Volt-Var
AO215 | Volt-Var Control Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.RvrtTms | AI293 | Volt-Var
AO216 | Volt-Var Control Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVVR.EcpRef | AI294 | Volt-Var | C: For Function, unless set at implementation
AO217 | Volt-Var Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVVR.VVArCrv | AI297 | Volt-Var | C: For Function | M
AO218 | Volt-Var Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.1 | AI298 | Volt-Var | C: For Function
AO219 | Volt-Var Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.2 | AI299 | Volt-Var | C: For Function
AO220 | Volt-Var Autonomous Voltage Reference Adjustment Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.VRefTmms | AI300 | Volt-Var | C: For Function | M
AO221 | Watt-Var Mode Priority | 0 | 100 | 1 | 0 | n/a | DWVR.ModPrio | AI302 | Watt-Var
AO222 | Watt-Var Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.WinTms | AI303 | Watt-Var
AO223 | Watt-Var Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.RmpTms | AI304 | Watt-Var
AO224 | Watt-Var Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.RvrtTms | AI305 | Watt-Var
AO225 | Watt-Var Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWVR.EcpRef | AI306 | Watt-Var | C: For Function, unless set at implementation
AO226 | Watt-Var Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DWVR.WVArCrv | AI308 | Watt-Var | C: For Function
AO227 | Watt-Var Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.1 | AI309 | Watt-Var | C: For Function
AO228 | Watt-Var Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.2 | AI310 | Watt-Var | C: For Function
AO229 | Power Factor Correction Mode Priority | 0 | 100 | 1 | 0 | n/a | DPFC.ModPrio | AI312 | PF Correct
AO230 | Power Factor Correction Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DPFC.WinTms | AI313 | PF Correct
AO231 | Power Factor Correction Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DPFC.RmpRte | AI314 | PF Correct
AO232 | Power Factor Correction Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DPFC.RvrtTms | AI315 | PF Correct
AO233 | Power Factor Correction Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DPFC.EcpRef | AI316 | PF Correct | C: For Function, unless set at implementation
AO234 | Power Factor Correction Average PF Target | -100 | 100 | 0.01 | 0 | None | DPFC.PFTrg | AI318 | PF Correct | C: For Function
AO235 | Power Factor Correction Lower PF Limit | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.min | AI319 | PF Correct | C: For Function
AO236 | Power Factor Correction Upper PF Limit | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.max | AI320 | PF Correct | C: For Function
AO237 | Pricing Mode Priority | 0 | 100 | 1 | 0 | None | DPRG.ModPrio | AI321 | Price
AO238 | Pricing Mode Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.WinTms | AI322 | Price
AO239 | Pricing Mode Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.RmpTms | AI323 | Price
AO240 | Pricing Mode Reversion Timeout period | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.RvrtTms | AI324 | Price
AO241 | Pricing Mode Setpoint | -2147483648 | 2147483647 | 0.01 | 0 | 100ths of local currency | DPRG.PrcRef | AI325 | Price
AO242 | Pricing Mode Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.OplTmsMax.1 | AI326 | Price
AO243 | Pricing Mode Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.OplTmsMax.2 | AI327 | Price
AO244 | Curve Edit Selector. Writing to this point selects which of the curves can currently be viewed and changed. | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | AI328 | Curve | C: See clause 1.7 | C: See clause 1.7
AO245 | Curve Type. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-Var <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | AI329 | Curve | C: See clause 1.7 | C: See clause 1.7
AO246 | Curve Number of Points | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | AI330 | Curve | C: See clause 1.7 | C: See clause 1.7
AO247 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time (milliseconds) <23> Celsius Temperature <29> Voltage (V) <33> Frequency (Hz) <38> Watts (W) <100> Price in hundredths of local currency <129> Percent Voltage <133> Percent Frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | AI331 | Curve | C: See clause 1.7 | C: See clause 1.7
AO248 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> Vars as percent of max Vars (VarMax) <3> Vars as percent of max available Vars (VarAval) <4> Vars as percent of max Watts (Wmax) - not used <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor <8> Volts as a percent of the nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage (V) <33> Frequency (Hz) <38> Watts (W) <99+> Other | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | AI332 | Curve | C: See clause 1.7 | C: See clause 1.7
AO249 | Curve Point 1 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | AI333 | Curve | C: See clause 1.7 | C: See clause 1.7
AO250 | Curve Point 1 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | AI334 | Curve | C: See clause 1.7 | C: See clause 1.7
AO251 | Curve Point 2 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | AI335 | Curve | C: See clause 1.7 | C: See clause 1.7
AO252 | Curve Point 2 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | AI336 | Curve | C: See clause 1.7 | C: See clause 1.7
AO253 | Curve Point 3 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | AI337 | Curve | C: See clause 1.7 | C: See clause 1.7
AO254 | Curve Point 3 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | AI338 | Curve | C: See clause 1.7 | C: See clause 1.7
AO255 | Curve Point 4 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | AI339 | Curve | C: See clause 1.7 | C: See clause 1.7
AO256 | Curve Point 4 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | AI340 | Curve | C: See clause 1.7 | C: See clause 1.7
AO257 | Curve Point 5 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.xVal | AI341 | Curve | C: See clause 1.7
AO258 | Curve Point 5 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.yVal | AI342 | Curve | C: See clause 1.7
AO259 | Curve Point 6 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.xVal | AI343 | Curve | C: See clause 1.7
AO260 | Curve Point 6 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.yVal | AI344 | Curve | C: See clause 1.7
AO261 | Curve Point 7 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.xVal | AI345 | Curve | C: See clause 1.7
AO262 | Curve Point 7 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.yVal | AI346 | Curve | C: See clause 1.7
AO263 | Curve Point 8 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.xVal | AI347 | Curve | C: See clause 1.7
AO264 | Curve Point 8 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.yVal | AI348 | Curve | C: See clause 1.7
AO265 | Curve Point 9 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.xVal | AI349 | Curve | C: See clause 1.7
AO266 | Curve Point 9 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.yVal | AI350 | Curve | C: See clause 1.7
AO267 | Curve Point 10 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.xVal | AI351 | Curve | C: See clause 1.7
AO268 | Curve Point 10 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.yVal | AI352 | Curve | C: See clause 1.7
AO269 | Curve Point 11 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.11.xVal | AI353 | Curve | C: See clause 1.7
AO270 | Curve Point 11 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.11.yVal | AI354 | Curve | C: See clause 1.7
AO271 | Curve Point 12 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.12.xVal | AI355 | Curve | C: See clause 1.7
AO272 | Curve Point 12 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.12.yVal | AI356 | Curve | C: See clause 1.7
AO273 | Curve Point 13 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.13.xVal | AI357 | Curve | C: See clause 1.7
AO274 | Curve Point 13 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.13.yVal | AI358 | Curve | C: See clause 1.7
AO275 | Curve Point 14 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.14.xVal | AI359 | Curve | C: See clause 1.7
AO276 | Curve Point 14 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.14.yVal | AI360 | Curve | C: See clause 1.7
AO277 | Curve Point 15 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.15.xVal | AI361 | Curve | C: See clause 1.7
AO278 | Curve Point 15 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.15.yVal | AI362 | Curve | C: See clause 1.7
AO279 | Curve Point 16 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.16.xVal | AI363 | Curve | C: See clause 1.7
AO280 | Curve Point 16 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.16.yVal | AI364 | Curve | C: See clause 1.7
AO281 | Curve Point 17 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.17.xVal | AI365 | Curve | C: See clause 1.7
AO282 | Curve Point 17 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.17.yVal | AI366 | Curve | C: See clause 1.7
AO283 | Curve Point 18 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.18.xVal | AI367 | Curve | C: See clause 1.7
AO284 | Curve Point 18 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.18.yVal | AI368 | Curve | C: See clause 1.7
AO285 | Curve Point 19 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.19.xVal | AI369 | Curve | C: See clause 1.7
AO286 | Curve Point 19 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.19.yVal | AI370 | Curve | C: See clause 1.7
AO287 | Curve Point 20 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.20.xVal | AI371 | Curve | C: See clause 1.7
AO288 | Curve Point 20 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.20.yVal | AI372 | Curve | C: See clause 1.7
AO289 | Curve Point 21 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.21.xVal | AI373 | Curve
AO290 | Curve Point 21 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.21.yVal | AI374 | Curve
AO291 | Curve Point 22 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.22.xVal | AI375 | Curve
AO292 | Curve Point 22 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.22.yVal | AI376 | Curve
AO293 | Curve Point 23 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.23.xVal | AI377 | Curve
AO294 | Curve Point 23 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.23.yVal | AI378 | Curve
AO295 | Curve Point 24 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.24.xVal | AI379 | Curve
AO296 | Curve Point 24 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.24.yVal | AI380 | Curve
AO297 | Curve Point 25 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.25.xVal | AI381 | Curve
AO298 | Curve Point 25 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.25.yVal | AI382 | Curve
AO299 | Curve Point 26 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.26.xVal | AI383 | Curve
AO300 | Curve Point 26 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.26.yVal | AI384 | Curve
AO301 | Curve Point 27 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.27.xVal | AI385 | Curve
AO302 | Curve Point 27 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.27.yVal | AI386 | Curve
AO303 | Curve Point 28 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.28.xVal | AI387 | Curve
AO304 | Curve Point 28 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.28.yVal | AI388 | Curve
AO305 | Curve Point 29 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.29.xVal | AI389 | Curve
AO306 | Curve Point 29 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.29.yVal | AI390 | Curve
AO307 | Curve Point 30 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.30.xVal | AI391 | Curve
AO308 | Curve Point 30 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.30.yVal | AI392 | Curve
AO309 | Curve Point 31 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.31.xVal | AI393 | Curve
AO310 | Curve Point 31 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.31.yVal | AI394 | Curve
AO311 | Curve Point 32 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.32.xVal | AI395 | Curve
AO312 | Curve Point 32 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.32.yVal | AI396 | Curve
AO313 | Curve Point 33 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.33.xVal | AI397 | Curve
AO314 | Curve Point 33 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.33.yVal | AI398 | Curve
AO315 | Curve Point 34 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.34.xVal | AI399 | Curve
AO316 | Curve Point 34 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.34.yVal | AI400 | Curve
AO317 | Curve Point 35 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.35.xVal | AI401 | Curve
AO318 | Curve Point 35 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.35.yVal | AI402 | Curve
AO319 | Curve Point 36 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.36.xVal | AI403 | Curve
AO320 | Curve Point 36 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.36.yVal | AI404 | Curve
AO321 | Curve Point 37 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.37.xVal | AI405 | Curve
AO322 | Curve Point 37 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.37.yVal | AI406 | Curve
AO323 | Curve Point 38 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.38.xVal | AI407 | Curve
AO324 | Curve Point 38 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.38.yVal | AI408 | Curve
AO325 | Curve Point 39 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.39.xVal | AI409 | Curve
AO326 | Curve Point 39 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.39.yVal | AI410 | Curve
AO327 | Curve Point 40 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.40.xVal | AI411 | Curve
AO328 | Curve Point 40 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.40.yVal | AI412 | Curve
AO329 | Curve Point 41 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.41.xVal | AI413 | Curve
AO330 | Curve Point 41 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.41.yVal | AI414 | Curve
AO331 | Curve Point 42 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.42.xVal | AI415 | Curve
AO332 | Curve Point 42 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.42.yVal | AI416 | Curve
AO333 | Curve Point 43 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.43.xVal | AI417 | Curve
AO334 | Curve Point 43 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.43.yVal | AI418 | Curve
AO335 | Curve Point 44 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.44.xVal | AI419 | Curve
AO336 | Curve Point 44 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.44.yVal | AI420 | Curve
AO337 | Curve Point 45 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.45.xVal | AI421 | Curve
AO338 | Curve Point 45 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.45.yVal | AI422 | Curve
AO339 | Curve Point 46 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.46.xVal | AI423 | Curve
AO340 | Curve Point 46 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.46.yVal | AI424 | Curve
AO341 | Curve Point 47 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.47.xVal | AI425 | Curve
AO342 | Curve Point 47 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.47.yVal | AI426 | Curve
AO343 | Curve Point 48 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.48.xVal | AI427 | Curve
AO344 | Curve Point 48 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.48.yVal | AI428 | Curve
AO345 | Curve Point 49 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.49.xVal | AI429 | Curve
AO346 | Curve Point 49 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.49.yVal | AI430 | Curve
AO347 | Curve Point 50 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.50.xVal | AI431 | Curve
AO348 | Curve Point 50 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.50.yVal | AI432 | Curve
AO349 | Curve Point 51 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.51.xVal | AI433 | Curve
AO350 | Curve Point 51 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.51.yVal | AI434 | Curve
AO351 | Curve Point 52 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.52.xVal | AI435 | Curve
AO352 | Curve Point 52 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.52.yVal | AI436 | Curve
AO353 | Curve Point 53 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.53.xVal | AI437 | Curve
AO354 | Curve Point 53 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.53.yVal | AI438 | Curve
AO355 | Curve Point 54 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.54.xVal | AI439 | Curve
AO356 | Curve Point 54 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.54.yVal | AI440 | Curve
AO357 | Curve Point 55 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.55.xVal | AI441 | Curve
AO358 | Curve Point 55 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.55.yVal | AI442 | Curve
AO359 | Curve Point 56 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.56.xVal | AI443 | Curve
AO360 | Curve Point 56 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.56.yVal | AI444 | Curve
AO361 | Curve Point 57 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.57.xVal | AI445 | Curve
AO362 | Curve Point 57 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.57.yVal | AI446 | Curve
AO363 | Curve Point 58 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.58.xVal | AI447 | Curve
AO364 | Curve Point 58 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.58.yVal | AI448 | Curve
AO365 | Curve Point 59 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.59.xVal | AI449 | Curve
AO366 | Curve Point 59 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.59.yVal | AI450 | Curve
AO367 | Curve Point 60 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.60.xVal | AI451 | Curve
AO368 | Curve Point 60 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.60.yVal | AI452 | Curve
AO369 | Curve Point 61 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.61.xVal | AI453 | Curve
AO370 | Curve Point 61 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.61.yVal | AI454 | Curve
AO371 | Curve Point 62 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.62.xVal | AI455 | Curve
AO372 | Curve Point 62 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.62.yVal | AI456 | Curve
AO373 | Curve Point 63 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.63.xVal | AI457 | Curve
AO374 | Curve Point 63 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.63.yVal | AI458 | Curve
AO375 | Curve Point 64 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.64.xVal | AI459 | Curve
AO376 | Curve Point 64 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.64.yVal | AI460 | Curve
AO377 | Curve Point 65 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.65.xVal | AI461 | Curve
AO378 | Curve Point 65 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.65.yVal | AI462 | Curve
AO379 | Curve Point 66 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.66.xVal | AI463 | Curve
AO380 | Curve Point 66 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.66.yVal | AI464 | Curve
AO381 | Curve Point 67 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.67.xVal | AI465 | Curve
AO382 | Curve Point 67 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.67.yVal | AI466 | Curve
AO383 | Curve Point 68 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.68.xVal | AI467 | Curve
AO384 | Curve Point 68 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.68.yVal | AI468 | Curve
AO385 | Curve Point 69 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.69.xVal | AI469 | Curve
AO386 | Curve Point 69 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.69.yVal | AI470 | Curve
AO387 | Curve Point 70 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.70.xVal | AI471 | Curve
AO388 | Curve Point 70 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.70.yVal | AI472 | Curve
AO389 | Curve Point 71 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.71.xVal | AI473 | Curve
AO390 | Curve Point 71 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.71.yVal | AI474 | Curve
AO391 | Curve Point 72 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.72.xVal | AI475 | Curve
AO392 | Curve Point 72 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.72.yVal | AI476 | Curve
AO393 | Curve Point 73 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.73.xVal | AI477 | Curve
AO394 | Curve Point 73 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.73.yVal | AI478 | Curve
AO395 | Curve Point 74 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.74.xVal | AI479 | Curve
AO396 | Curve Point 74 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.74.yVal | AI480 | Curve
AO397 | Curve Point 75 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.75.xVal | AI481 | Curve
AO398 | Curve Point 75 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.75.yVal | AI482 | Curve
AO399 | Curve Point 76 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.76.xVal | AI483 | Curve
AO400 | Curve Point 76 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.76.yVal | AI484 | Curve
AO401 | Curve Point 77 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.77.xVal | AI485 | Curve
AO402 | Curve Point 77 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.77.yVal | AI486 | Curve
AO403 | Curve Point 78 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.78.xVal | AI487 | Curve
AO404 | Curve Point 78 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.78.yVal | AI488 | Curve
AO405 | Curve Point 79 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.79.xVal | AI489 | Curve
AO406 | Curve Point 79 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.79.yVal | AI490 | Curve
AO407 | Curve Point 80 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.80.xVal | AI491 | Curve
AO408 | Curve Point 80 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.80.yVal | AI492 | Curve
AO409 | Curve Point 81 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.81.xVal | AI493 | Curve
AO410 | Curve Point 81 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.81.yVal | AI494 | Curve
AO411 | Curve Point 82 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.82.xVal | AI495 | Curve
AO412 | Curve Point 82 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.82.yVal | AI496 | Curve
AO413 | Curve Point 83 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.83.xVal | AI497 | Curve
AO414 | Curve Point 83 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.83.yVal | AI498 | Curve
AO415 | Curve Point 84 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.84.xVal | AI499 | Curve
AO416 | Curve Point 84 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.84.yVal | AI500 | Curve
AO417 | Curve Point 85 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.85.xVal | AI501 | Curve
AO418 | Curve Point 85 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.85.yVal | AI502 | Curve
AO419 | Curve Point 86 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.86.xVal | AI503 | Curve
AO420 | Curve Point 86 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.86.yVal | AI504 | Curve
AO421 | Curve Point 87 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.87.xVal | AI505 | Curve
AO422 | Curve Point 87 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.87.yVal | AI506 | Curve
AO423 | Curve Point 88 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.88.xVal | AI507 | Curve
AO424 | Curve Point 88 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.88.yVal | AI508 | Curve
AO425 | Curve Point 89 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.89.xVal | AI509 | Curve
AO426 | Curve Point 89 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.89.yVal | AI510 | Curve
AO427 | Curve Point 90 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.90.xVal | AI511 | Curve
AO428 | Curve Point 90 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.90.yVal | AI512 | Curve
AO429 | Curve Point 91 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.91.xVal | AI513 | Curve
AO430 | Curve Point 91 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.91.yVal | AI514 | Curve
AO431 | Curve Point 92 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.92.xVal | AI515 | Curve
AO432 | Curve Point 92 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.92.yVal | AI516 | Curve
AO433 | Curve Point 93 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.93.xVal | AI517 | Curve
AO434 | Curve Point 93 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.93.yVal | AI518 | Curve
AO435 | Curve Point 94 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.94.xVal | AI519 | Curve
AO436 | Curve Point 94 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.94.yVal | AI520 | Curve
AO437 | Curve Point 95 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.95.xVal | AI521 | Curve
AO438 | Curve Point 95 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.95.yVal | AI522 | Curve
AO439 | Curve Point 96 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.96.xVal | AI523 | Curve
AO440 | Curve Point 96 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.96.yVal | AI524 | Curve
AO441 | Curve Point 97 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.97.xVal | AI525 | Curve
AO442 | Curve Point 97 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.97.yVal | AI526 | Curve
AO443 | Curve Point 98 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.98.xVal | AI527 | Curve
AO444 | Curve Point 98 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.98.yVal | AI528 | Curve
AO445 | Curve Point 99 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.99.xVal | AI529 | Curve
AO446 | Curve Point 99 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.99.yVal | AI530 | Curve
AO447 | Curve Point 100 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.100.xVal | AI531 | Curve
AO448 | Curve Point 100 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.100.yVal | AI532 | Curve
AO449 | System Meter Active Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | MMXU0.TotW.rangeC.hLim | AI557 | Monitoring
AO450 | System Meter Active Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | MMXU0.TotW.rangeC.lLim | AI558 | Monitoring
AO451 | System Meter Reactive Power – High Threshold | 0 | 2147483647 | 1 | 0 | var | MMXU0.TotVAr.rangeC.hLim | AI559 | Monitoring
AO452 | System Meter at Reactive Power – Low Threshold | 0 | 2147483647 | 1 | 0 | var | MMXU0.TotVAr.rangeC.lLim | AI560 | Monitoring
AO453 | System Meter at Power Factor – High Threshold | -100 | 100 | 0.01 | 0 | None | MMXU0.TotPF.rangeC.hLim | AI561 | Monitoring
AO454 | System Meter at Power Factor – Low Threshold | -100 | 100 | 0.01 | 0 | None | MMXU0.TotPF.rangeC.lLim | AI562 | Monitoring
AO455 | System Meter Phase A Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | MMXU0.PhV.phsA.rangeC.hLim | AI563 | Monitoring
AO456 | System Meter Phase A Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | MMXU0.PhV.phsA.rangeC.lLim | AI564 | Monitoring
AO457 | System Meter Phase B Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | MMXU0.PhV.phsB.rangeC.hLim | AI565 | Monitoring
AO458 | System Meter Phase B Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | MMXU0.PhV.phsB.rangeC.lLim | AI566 | Monitoring
AO459 | System Meter Phase C Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | MMXU0.PhV.phsC.rangeC.hLim | AI567 | Monitoring
AO460 | System Meter Phase C Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | MMXU0.PhV.phsC.rangeC.lLim | AI568 | Monitoring
AO473 | Renewable energy source. Max rated active power (WMaxRtg) which may result from renewable energy resource | 0 | 2147483647 | 1 | 0 | Watts | RenWMaxRtg | AI582 | Renewable energy source | C: For Function
AO474 | Max SOC for Active Power Following #1 (Peak Power Limiting) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMaxPct | AI584 | Peak Power Limiting | C: For Function
AO475 | Min SOC for Active Power Following #1 (Peak Power Limiting) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMinPct | AI585 | Peak Power Limiting | C: For Function
AO476 | Max SOC for Active Power Following #2 (Load Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMaxPct | AI586 | Load Following | C: For Function
AO477 | Min SOC for Active Power Following #2 (Load Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMinPct | AI587 | Load Following | C: For Function
AO478 | Max SOC for Active Power Following #3 (Generation Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMaxPct | AI588 | Generation Following | C: For Function
AO479 | Min SOC for Active Power Following #3 (Generation Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMinPct | AI589 | Generation Following | C: For Function
AO480 | High Frequency-Watt Droop Upper Gradient | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | AI590 | Droop Freq-Watt | C: For Function | M
AO481 | Low Frequency-Watt Droop Lower Gradient | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | AI591 | Droop Freq-Watt | C: For Function | M
AO482 | High Frequency-Watt Droop Minimum Active Power | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | AI592 | Droop Freq-Watt | C: For Function | M
AO483 | Low Frequency-Watt Droop Maximum Active Power | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | AI593 | Droop Freq-Watt | C: For Function | M
AO484 | Volt-Var 4 V-Q pairs Volt V1 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt1 | AI594 | Volt-Var | C: For Function
AO485 | Volt-Var 4 V-Q pairs Vars Q1 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt1 | AI595 | Volt-Var | C: For Function
AO486 | Volt-Var 4 V-Q pairs Volt V2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt2 | AI596 | Volt-Var | C: For Function
AO487 | Volt-Var 4 V-Q pairs Vars Q2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt2 | AI597 | Volt-Var | C: For Function
AO488 | Volt-Var 4 V-Q pairs Volt V3 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt3 | AI598 | Volt-Var | C: For Function
AO489 | Volt-Var 4 V-Q pairs Vars Q3 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt3 | AI599 | Volt-Var | C: For Function
AO490 | Volt-Var 4 V-Q pairs Volt V4 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt4 | AI600 | Volt-Var | C: For Function
AO491 | Volt-Var 4 V-Q pairs Vars Q4 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt4 | AI601 | Volt-Var | C: For Function
AO492 | Watt-Var 4 P-Q pairs Watt P1 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt1 | AI602 | Watt-Var | C: For Function
AO493 | Watt-Var 4 P-Q pairs Vars Q1 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt1 | AI603 | Watt-Var | C: For Function
AO494 | Watt-Var 4 P-Q pairs Watt P2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt2 | AI604 | Watt-Var | C: For Function
AO495 | Watt-Var 4 P-Q pairs Vars Q2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt2 | AI605 | Watt-Var | C: For Function
AO496 | Watt-Var 4 P-Q pairs Watt P3 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt3 | AI606 | Watt-Var | C: For Function
AO497 | Watt-Var 4 P-Q pairs Vars Q3 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt3 | AI607 | Watt-Var | C: For Function
AO498 | Watt-Var 4 P-Q pairs Watt P4 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt4 | AI608 | Watt-Var | C: For Function
AO499 | Watt-Var 4 P-Q pairs Vars Q4 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt4 | AI609 | Watt-Var | C: For Function
AO500 | Volt-Watt 2 V-P pairs Volt V1 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC.VPctPt1 | AI610 | Volt-Watt | C: For Function
AO501 | Volt-Watt 2 V-P pairs Watt P1 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC.WPctPt1 | AI611 | Volt-Watt | C: For Function
AO502 | Volt-Watt 2 V-P pairs Volt V2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC.VPctPt2 | AI612 | Volt-Watt | C: For Function
AO503 | Volt-Watt 2 V-P pairs Watt P2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC.WPctPt2 | AI613 | Volt-Watt | C: For Function
AO504 | Volt-Watt 2 V-P pairs Volt V3 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC.VPctPt3 | AI614 | Volt-Watt
AO505 | Volt-Watt 2 V-P pairs Watt P3 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC.WPctPt3 | AI615 | Volt-Watt
AO506 | Volt-Watt 2 V-P pairs Volt V4 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC.VPctPt4 | AI616 | Volt-Watt
AO507 | Volt-Watt 2 V-P pairs Watt P4 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC.WPctPt4 | AI617 | Volt-Watt
AO508 | Charge/Discharge target in Watts | -2147483648 | 2147483647 | 1 | 0 | Watts | DWGC.GnWSpt | AI618 | Charge/Discharge | C: For Function If BI114=1
AO509 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | AI619 | Active Power Limit | C: For Function if BI113 = 1 | M
AO510 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | AI620 | Active Power Limit | C: For Function if BI113 = 1 | M
AO511 | Constant Vars using vars as unit | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | AI621 | Constant Vars | C: For Function if BI115 = 1 | M
AO600 | Counter units. ENUM 1 = WHr, 2 = kWhr, 3 = MWHr | 1 | 3 | 1 | 0 | Enum | MESA.Ctr.Units | AI622 | Counters
AO2000 | Schedule to Edit Selector. Selects which of the schedules can be currently viewed and changed. | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCC.Schd | AI2001 | BC Scheduling | C: For Back Comp
AO2001 | Selected Schedule Identity | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCCn.Schd | AI2002 | BC Scheduling | C: For Back Comp
AO2002 | Selected Schedule Priority. Priority of the schedule relative to other running schedules. Lower values have higher priority over higher values. | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCHn.SchdPrio | AI2003 | BC Scheduling | C: For Back Comp
AO2003 | Selected Schedule Type. Enumeration: <1> Low/High Voltage Ride-Through – Hi Must Trip <2> Low/High Voltage Ride-Through – Low Must Trip <3> Low/High Voltage Ride-Through – Hi Momentary <4> Low/High Voltage Ride-Through – Lo Momentary <5> Low/High Frequency Ride-Through – Hi Must Trip <6> Low/High Frequency Ride-Through – Lo Must Trip <7> Low/High Frequency Ride-Through – Hi Momentary <8> Low/High Frequency Ride-Through – Low Momentary <9> Dynamic Reactive Current Support - On/Off <10> Dynamic Volt-Watt - On/Off <11> Frequency-Watt - On/Off <12> Active Power Limit - Charging <13> Active Power Limit - Discharging <14> Charge/Discharge - Percent of Maximum <15> Coordinated Charge/Discharge - SOC Target <16> Active Power Response #1 - On/Off <17> Active Power Response #2 - On/Off <18> Active Power Response #3 - On/Off <19> AGC – Watts <20> Active Power Smoothing - On/Off <21> Volt-Watt – Curve Index <22> Frequency-Watt Curve – Curve Index <23> Frequency-Watt Curve – High Hysteresis <24> Frequency-Watt Curve – Low Hysteresis <25> Constant VArs - Percent of Maximum <26> Constant Power Factor - Power Factor <27> Volt-VAr – Curve Index <28> Watt-VAr – Curve Index <29> Power Factor Correction - On/Off <30> Reserved - For pricing mode <31> Charge/Discharge - enable/disable <32> Coordinated Charge/Discharge - enable/disable <33> Active Power Limit - Discharging - enable/disable <34> Active Power Response #1 - Limit <35> Active Power Response #2 - Limit <36> Active Power Response #3 - Limit <37> AGC - enable/disable ... <100> Vendor-specific enumerations above | 0 | 255 | 1 | 0 | Enum | MESAn.SchdVal.valEq | AI2004 | BC Scheduling | C: For Back Comp
AO2004 | Selected Schedule Start Date. Number of days since January 1, 1970, UTC. | 0 | 2147483647 | 1 | 0 | Days | BC.FSCHn.StrTm.Date | AI2005 | BC Scheduling | C: For Back Comp
AO2005 | Selected Schedule Start Time. Milliseconds since the start of Schedule Start Date. | 0 | 86400000 | 1 | 0 | milliseconds | BC.FSCHn.StrTm.Time | AI2006 | BC Scheduling | C: For Back Comp
AO2006 | Selected Schedule Repeat Interval. Interval between actions after the initial occurrence. A zero value means the schedule is not repeated. | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCHn.NxtStrTm | AI2007 | BC Scheduling | C: For Back Comp
AO2007 | Selected Schedule Repeat Interval Units. Enumeration: <0> = No Repeat <1> = Seconds <2> = Minutes <3> = Hours <4> = Days <5> = Weeks <6> = Months <7> = Months on Same Day of Week <8> = Months on Same Day of Week from End | 0 | 8 | 1 | 0 | Enum | BC.FSCHn.SchdReuse | AI2008 | BC Scheduling | C: For Back Comp
AO2008 | Selected Schedule Number of Points | 0 | 100 | 1 | 0 | n/a | BC.FSCHn.NumEntr | AI2011 | BC Scheduling | C: For Back Comp
AO2009 | Selected Schedule Point [1] Time Offset. Number of seconds from the start of the schedule when this point becomes active. | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.1 | AI2012 | BC Scheduling | C: For Back Comp
AO2010 | Selected Schedule Point [1] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.1 | AI2013 | BC Scheduling | C: For Back Comp
AO2011 | Selected Schedule Point [2] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.2 | AI2014 | BC Scheduling | C: For Back Comp
AO2012 | Selected Schedule Point [2] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.2 | AI2015 | BC Scheduling | C: For Back Comp
AO2013 | Selected Schedule Point [3] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.3 | AI2016 | BC Scheduling | C: For Back Comp
AO2014 | Selected Schedule Point [3] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.3 | AI2017 | BC Scheduling | C: For Back Comp
AO2015 | Selected Schedule Point [4] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.4 | AI2018 | BC Scheduling | C: For Back Comp
AO2016 | Selected Schedule Point [4] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.4 | AI2019 | BC Scheduling | C: For Back Comp
AO2017 | Selected Schedule Point [5] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.5 | AI2020 | BC Scheduling | C: For Back Comp
AO2018 | Selected Schedule Point [5] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.5 | AI2021 | BC Scheduling | C: For Back Comp
AO2019 | Selected Schedule Point [6] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.6 | AI2022 | BC Scheduling | C: For Back Comp
AO2020 | Selected Schedule Point [6] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.6 | AI2023 | BC Scheduling | C: For Back Comp
AO2021 | Selected Schedule Point [7] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.7 | AI2024 | BC Scheduling | C: For Back Comp
AO2022 | Selected Schedule Point [7] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.7 | AI2025 | BC Scheduling | C: For Back Comp
AO2023 | Selected Schedule Point [8] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.8 | AI2026 | BC Scheduling | C: For Back Comp
AO2024 | Selected Schedule Point [8] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.8 | AI2027 | BC Scheduling | C: For Back Comp
AO2025 | Selected Schedule Point [9] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.9 | AI2028 | BC Scheduling | C: For Back Comp
AO2026 | Selected Schedule Point [9] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.9 | AI2029 | BC Scheduling | C: For Back Comp
AO2027 | Selected Schedule Point [10] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.10 | AI2030 | BC Scheduling | C: For Back Comp
AO2028 | Selected Schedule Point [10] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.10 | AI2031 | BC Scheduling | C: For Back Comp
AO2029 | Selected Schedule Point [11] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.11 | AI2032 | BC Scheduling | C: For Back Comp
AO2030 | Selected Schedule Point [11] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.11 | AI2033 | BC Scheduling | C: For Back Comp
AO2031 | Selected Schedule Point [12] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.12 | AI2034 | BC Scheduling | C: For Back Comp
AO2032 | Selected Schedule Point [12] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.12 | AI2035 | BC Scheduling | C: For Back Comp
AO2033 | Selected Schedule Point [13] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.13 | AI2036 | BC Scheduling | C: For Back Comp
AO2034 | Selected Schedule Point [13] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.13 | AI2037 | BC Scheduling | C: For Back Comp
AO2035 | Selected Schedule Point [14] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.14 | AI2038 | BC Scheduling | C: For Back Comp
AO2036 | Selected Schedule Point [14] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.14 | AI2039 | BC Scheduling | C: For Back Comp
AO2037 | Selected Schedule Point [15] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.15 | AI2040 | BC Scheduling | C: For Back Comp
AO2038 | Selected Schedule Point [15] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.15 | AI2041 | BC Scheduling | C: For Back Comp
AO2039 | Selected Schedule Point [16] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.16 | AI2042 | BC Scheduling | C: For Back Comp
AO2040 | Selected Schedule Point [16] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.16 | AI2043 | BC Scheduling | C: For Back Comp
AO2041 | Selected Schedule Point [17] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.17 | AI2044 | BC Scheduling | C: For Back Comp
AO2042 | Selected Schedule Point [17] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.17 | AI2045 | BC Scheduling | C: For Back Comp
AO2043 | Selected Schedule Point [18] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.18 | AI2046 | BC Scheduling | C: For Back Comp
AO2044 | Selected Schedule Point [18] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.18 | AI2047 | BC Scheduling | C: For Back Comp
AO2045 | Selected Schedule Point [19] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.19 | AI2048 | BC Scheduling | C: For Back Comp
AO2046 | Selected Schedule Point [19] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.19 | AI2049 | BC Scheduling | C: For Back Comp
AO2047 | Selected Schedule Point [20] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.20 | AI2050 | BC Scheduling | C: For Back Comp
AO2048 | Selected Schedule Point [20] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.20 | AI2051 | BC Scheduling | C: For Back Comp
AO2049 | Selected Schedule Point [21] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.21 | AI2052 | BC Scheduling
AO2050 | Selected Schedule Point [21] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.21 | AI2053 | BC Scheduling
AO2051 | Selected Schedule Point [22] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.22 | AI2054 | BC Scheduling
AO2052 | Selected Schedule Point [22] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.22 | AI2055 | BC Scheduling
AO2053 | Selected Schedule Point [23] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.23 | AI2056 | BC Scheduling
AO2054 | Selected Schedule Point [23] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.23 | AI2057 | BC Scheduling
AO2055 | Selected Schedule Point [24] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.24 | AI2058 | BC Scheduling
AO2056 | Selected Schedule Point [24] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.24 | AI2059 | BC Scheduling
AO2057 | Selected Schedule Point [25] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.25 | AI2060 | BC Scheduling
AO2058 | Selected Schedule Point [25] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.25 | AI2061 | BC Scheduling
AO2059 | Selected Schedule Point [26] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.26 | AI2062 | BC Scheduling
AO2060 | Selected Schedule Point [26] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.26 | AI2063 | BC Scheduling
AO2061 | Selected Schedule Point [27] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.27 | AI2064 | BC Scheduling
AO2062 | Selected Schedule Point [27] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.27 | AI2065 | BC Scheduling
AO2063 | Selected Schedule Point [28] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.28 | AI2066 | BC Scheduling
AO2064 | Selected Schedule Point [28] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.28 | AI2067 | BC Scheduling
AO2065 | Selected Schedule Point [29] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.29 | AI2068 | BC Scheduling
AO2066 | Selected Schedule Point [29] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.29 | AI2069 | BC Scheduling
AO2067 | Selected Schedule Point [30] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.30 | AI2070 | BC Scheduling
AO2068 | Selected Schedule Point [30] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.30 | AI2071 | BC Scheduling
AO2069 | Selected Schedule Point [31] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.31 | AI2072 | BC Scheduling
AO2070 | Selected Schedule Point [31] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.31 | AI2073 | BC Scheduling
AO2071 | Selected Schedule Point [32] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.32 | AI2074 | BC Scheduling
AO2072 | Selected Schedule Point [32] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.32 | AI2075 | BC Scheduling
AO2073 | Selected Schedule Point [33] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.33 | AI2076 | BC Scheduling
AO2074 | Selected Schedule Point [33] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.33 | AI2077 | BC Scheduling
AO2075 | Selected Schedule Point [34] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.34 | AI2078 | BC Scheduling
AO2076 | Selected Schedule Point [34] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.34 | AI2079 | BC Scheduling
AO2077 | Selected Schedule Point [35] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.35 | AI2080 | BC Scheduling
AO2078 | Selected Schedule Point [35] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.35 | AI2081 | BC Scheduling
AO2079 | Selected Schedule Point [36] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.36 | AI2082 | BC Scheduling
AO2080 | Selected Schedule Point [36] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.36 | AI2083 | BC Scheduling
AO2081 | Selected Schedule Point [37] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.37 | AI2084 | BC Scheduling
AO2082 | Selected Schedule Point [37] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.37 | AI2085 | BC Scheduling
AO2083 | Selected Schedule Point [38] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.38 | AI2086 | BC Scheduling
AO2084 | Selected Schedule Point [38] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.38 | AI2087 | BC Scheduling
AO2085 | Selected Schedule Point [39] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.39 | AI2088 | BC Scheduling
AO2086 | Selected Schedule Point [39] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.39 | AI2089 | BC Scheduling
AO2087 | Selected Schedule Point [40] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.40 | AI2090 | BC Scheduling
AO2088 | Selected Schedule Point [40] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.40 | AI2091 | BC Scheduling
AO2089 | Selected Schedule Point [41] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.41 | AI2092 | BC Scheduling
AO2090 | Selected Schedule Point [41] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.41 | AI2093 | BC Scheduling
AO2091 | Selected Schedule Point [42] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.42 | AI2094 | BC Scheduling
AO2092 | Selected Schedule Point [42] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.42 | AI2095 | BC Scheduling
AO2093 | Selected Schedule Point [43] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.43 | AI2096 | BC Scheduling
AO2094 | Selected Schedule Point [43] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.43 | AI2097 | BC Scheduling
AO2095 | Selected Schedule Point [44] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.44 | AI2098 | BC Scheduling
AO2096 | Selected Schedule Point [44] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.44 | AI2099 | BC Scheduling
AO2097 | Selected Schedule Point [45] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.45 | AI2100 | BC Scheduling
AO2098 | Selected Schedule Point [45] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.45 | AI2101 | BC Scheduling
AO2099 | Selected Schedule Point [46] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.46 | AI2102 | BC Scheduling
AO2100 | Selected Schedule Point [46] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.46 | AI2103 | BC Scheduling
AO2101 | Selected Schedule Point [47] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.47 | AI2104 | BC Scheduling
AO2102 | Selected Schedule Point [47] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.47 | AI2105 | BC Scheduling
AO2103 | Selected Schedule Point [48] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.48 | AI2106 | BC Scheduling
AO2104 | Selected Schedule Point [48] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.48 | AI2107 | BC Scheduling
AO2105 | Selected Schedule Point [49] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.49 | AI2108 | BC Scheduling
AO2106 | Selected Schedule Point [49] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.49 | AI2109 | BC Scheduling
AO2107 | Selected Schedule Point [50] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.50 | AI2110 | BC Scheduling
AO2108 | Selected Schedule Point [50] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.50 | AI2111 | BC Scheduling
AO2109 | Selected Schedule Point [51] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.51 | AI2112 | BC Scheduling
AO2110 | Selected Schedule Point [51] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.51 | AI2113 | BC Scheduling
AO2111 | Selected Schedule Point [52] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.52 | AI2114 | BC Scheduling
AO2112 | Selected Schedule Point [52] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.52 | AI2115 | BC Scheduling
AO2113 | Selected Schedule Point [53] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.53 | AI2116 | BC Scheduling
AO2114 | Selected Schedule Point [53] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.53 | AI2117 | BC Scheduling
AO2115 | Selected Schedule Point [54] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.54 | AI2118 | BC Scheduling
AO2116 | Selected Schedule Point [54] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.54 | AI2119 | BC Scheduling
AO2117 | Selected Schedule Point [55] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.55 | AI2120 | BC Scheduling
AO2118 | Selected Schedule Point [55] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.55 | AI2121 | BC Scheduling
AO2119 | Selected Schedule Point [56] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.56 | AI2122 | BC Scheduling
AO2120 | Selected Schedule Point [56] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.56 | AI2123 | BC Scheduling
AO2121 | Selected Schedule Point [57] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.57 | AI2124 | BC Scheduling
AO2122 | Selected Schedule Point [57] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.57 | AI2125 | BC Scheduling
AO2123 | Selected Schedule Point [58] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.58 | AI2126 | BC Scheduling
AO2124 | Selected Schedule Point [58] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.58 | AI2127 | BC Scheduling
AO2125 | Selected Schedule Point [59] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.59 | AI2128 | BC Scheduling
AO2126 | Selected Schedule Point [59] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.59 | AI2129 | BC Scheduling
AO2127 | Selected Schedule Point [60] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.60 | AI2130 | BC Scheduling
AO2128 | Selected Schedule Point [60] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.60 | AI2131 | BC Scheduling
AO2129 | Selected Schedule Point [61] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.61 | AI2132 | BC Scheduling
AO2130 | Selected Schedule Point [61] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.61 | AI2133 | BC Scheduling
AO2131 | Selected Schedule Point [62] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.62 | AI2134 | BC Scheduling
AO2132 | Selected Schedule Point [62] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.62 | AI2135 | BC Scheduling
AO2133 | Selected Schedule Point [63] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.63 | AI2136 | BC Scheduling
AO2134 | Selected Schedule Point [63] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.63 | AI2137 | BC Scheduling
AO2135 | Selected Schedule Point [64] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.64 | AI2138 | BC Scheduling
AO2136 | Selected Schedule Point [64] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.64 | AI2139 | BC Scheduling
AO2137 | Selected Schedule Point [65] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.65 | AI2140 | BC Scheduling
AO2138 | Selected Schedule Point [65] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.65 | AI2141 | BC Scheduling
AO2139 | Selected Schedule Point [66] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.66 | AI2142 | BC Scheduling
AO2140 | Selected Schedule Point [66] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.66 | AI2143 | BC Scheduling
AO2141 | Selected Schedule Point [67] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.67 | AI2144 | BC Scheduling
AO2142 | Selected Schedule Point [67] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.67 | AI2145 | BC Scheduling
AO2143 | Selected Schedule Point [68] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.68 | AI2146 | BC Scheduling
AO2144 | Selected Schedule Point [68] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.68 | AI2147 | BC Scheduling
AO2145 | Selected Schedule Point [69] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.69 | AI2148 | BC Scheduling
AO2146 | Selected Schedule Point [69] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.69 | AI2149 | BC Scheduling
AO2147 | Selected Schedule Point [70] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.70 | AI2150 | BC Scheduling
AO2148 | Selected Schedule Point [70] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.70 | AI2151 | BC Scheduling
AO2149 | Selected Schedule Point [71] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.71 | AI2152 | BC Scheduling
AO2150 | Selected Schedule Point [71] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.71 | AI2153 | BC Scheduling
AO2151 | Selected Schedule Point [72] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.72 | AI2154 | BC Scheduling
AO2152 | Selected Schedule Point [72] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.72 | AI2155 | BC Scheduling
AO2153 | Selected Schedule Point [73] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.73 | AI2156 | BC Scheduling
AO2154 | Selected Schedule Point [73] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.73 | AI2157 | BC Scheduling
AO2155 | Selected Schedule Point [74] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.74 | AI2158 | BC Scheduling
AO2156 | Selected Schedule Point [74] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.74 | AI2159 | BC Scheduling
AO2157 | Selected Schedule Point [75] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.75 | AI2160 | BC Scheduling
AO2158 | Selected Schedule Point [75] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.75 | AI2161 | BC Scheduling
AO2159 | Selected Schedule Point [76] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.76 | AI2162 | BC Scheduling
AO2160 | Selected Schedule Point [76] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.76 | AI2163 | BC Scheduling
AO2161 | Selected Schedule Point [77] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.77 | AI2164 | BC Scheduling
AO2162 | Selected Schedule Point [77] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.77 | AI2165 | BC Scheduling
AO2163 | Selected Schedule Point [78] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.78 | AI2166 | BC Scheduling
AO2164 | Selected Schedule Point [78] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.78 | AI2167 | BC Scheduling
AO2165 | Selected Schedule Point [79] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.79 | AI2168 | BC Scheduling
AO2166 | Selected Schedule Point [79] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.79 | AI2169 | BC Scheduling
AO2167 | Selected Schedule Point [80] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.80 | AI2170 | BC Scheduling
AO2168 | Selected Schedule Point [80] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.80 | AI2171 | BC Scheduling
AO2169 | Selected Schedule Point [81] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.81 | AI2172 | BC Scheduling
AO2170 | Selected Schedule Point [81] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.81 | AI2173 | BC Scheduling
AO2171 | Selected Schedule Point [82] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.82 | AI2174 | BC Scheduling
AO2172 | Selected Schedule Point [82] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.82 | AI2175 | BC Scheduling
AO2173 | Selected Schedule Point [83] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.83 | AI2176 | BC Scheduling
AO2174 | Selected Schedule Point [83] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.83 | AI2177 | BC Scheduling
AO2175 | Selected Schedule Point [84] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.84 | AI2178 | BC Scheduling
AO2176 | Selected Schedule Point [84] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.84 | AI2179 | BC Scheduling
AO2177 | Selected Schedule Point [85] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.85 | AI2180 | BC Scheduling
AO2178 | Selected Schedule Point [85] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.85 | AI2181 | BC Scheduling
AO2179 | Selected Schedule Point [86] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.86 | AI2182 | BC Scheduling
AO2180 | Selected Schedule Point [86] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.86 | AI2183 | BC Scheduling
AO2181 | Selected Schedule Point [87] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.87 | AI2184 | BC Scheduling
AO2182 | Selected Schedule Point [87] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.87 | AI2185 | BC Scheduling
AO2183 | Selected Schedule Point [88] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.88 | AI2186 | BC Scheduling
AO2184 | Selected Schedule Point [88] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.88 | AI2187 | BC Scheduling
AO2185 | Selected Schedule Point [89] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.89 | AI2188 | BC Scheduling
AO2186 | Selected Schedule Point [89] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.89 | AI2189 | BC Scheduling
AO2187 | Selected Schedule Point [90] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.90 | AI2190 | BC Scheduling
AO2188 | Selected Schedule Point [90] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.90 | AI2191 | BC Scheduling
AO2189 | Selected Schedule Point [91] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.91 | AI2192 | BC Scheduling
AO2190 | Selected Schedule Point [91] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.91 | AI2193 | BC Scheduling
AO2191 | Selected Schedule Point [92] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.92 | AI2194 | BC Scheduling
AO2192 | Selected Schedule Point [92] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.92 | AI2195 | BC Scheduling
AO2193 | Selected Schedule Point [93] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.93 | AI2196 | BC Scheduling
AO2194 | Selected Schedule Point [93] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.93 | AI2197 | BC Scheduling
AO2195 | Selected Schedule Point [94] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.94 | AI2198 | BC Scheduling
AO2196 | Selected Schedule Point [94] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.94 | AI2199 | BC Scheduling
AO2197 | Selected Schedule Point [95] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.95 | AI2200 | BC Scheduling
AO2198 | Selected Schedule Point [95] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.95 | AI2201 | BC Scheduling
AO2199 | Selected Schedule Point [96] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.96 | AI2202 | BC Scheduling
AO2200 | Selected Schedule Point [96] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.96 | AI2203 | BC Scheduling
AO2201 | Selected Schedule Point [97] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.97 | AI2204 | BC Scheduling
AO2202 | Selected Schedule Point [97] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.97 | AI2205 | BC Scheduling
AO2203 | Selected Schedule Point [98] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.98 | AI2206 | BC Scheduling
AO2204 | Selected Schedule Point [98] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.98 | AI2207 | BC Scheduling
AO2205 | Selected Schedule Point [99] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.99 | AI2208 | BC Scheduling
AO2206 | Selected Schedule Point [99] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.99 | AI2209 | BC Scheduling
AO2207 | Selected Schedule Point [100] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.100 | AI2210 | BC Scheduling
AO2208 | Selected Schedule Point [100] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.100 | AI2211 | BC Scheduling
AO3000 | Schedule Index to Edit Selector. Selection of Schedule Index for viewing, creating, and updating that schedule | 0 | 2147483647 | 1 | 0 | n/a | FSCC.Schd | AI3000 | Scheduling | C: For Sched
AO3001 | Selected Schedule Identity. Assigned ID of the schedule which may be different from the Schedule Index | 0 | 2147483647 | 1 | 0 | n/a | FSCCn.Schd | AI3001 | Scheduling | C: For Sched
AO3002 | Selected Schedule Priority. Priority of the schedule relative to other running schedules. Lower values have higher priority over higher values. | 0 | 2147483647 | 1 | 0 | n/a | FSCHn.SchdPrio | AI3002 | Scheduling | C: For Sched
AO3003 | Selected Schedule Start Date. Number of days since January 1, 1970, UTC. | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | AI3003 | Scheduling | C: For Sched
AO3004 | Selected Schedule Start Time. Seconds since the start of Schedule Start Date. | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | AI3004 | Scheduling | C: For Sched
AO3005 | Selected Schedule Stop Date. Number of days since January 1, 1970, UTC. | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | AI3005 | Scheduling | C: For Sched
AO3006 | Selected Schedule Stop Time. Seconds since the stop of Schedule Stop Date. | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | AI3006 | Scheduling | C: For Sched
AO3007 | Selected Schedule Repeat Interval. Interval between actions after the initial occurrence. A zero value means the schedule is not repeated. | 0 | 2147483647 | 1 | 0 | n/a | FSCHn.NxtStrTm | AI3007 | Scheduling | C: For Sched
AO3008 | Selected Schedule Repeat Interval Units. Enumeration: <0> = No Repeat <1> = Seconds <2> = Minutes <3> = Hours <4> = Days <5> = Weeks <6> = Months <7> = Months on Same Day of Week <8> = Months on Same Day of Week from End | 0 | 8 | 1 | 0 | Enum | FSCHn.SchdReuse | AI3008 | Scheduling | C: For Sched
AO3009 | Selected Schedule Number of Points | 0 | 100 | 1 | 0 | n/a | FSCHn.NumEntr | AI3011 | Scheduling | C: For Sched
AO3010 | Selected Schedule Point [1] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.1 | AI3012 | Scheduling | C: For Sched
AO3011 | Selected Schedule Point [1] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.1 | AI3013 | Scheduling | C: For Sched
AO3012 | Selected Schedule Point [1] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.1 | AI3014 | Scheduling | C: For Sched
AO3013 | Selected Schedule Point [1] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.1 | AI3015 | Scheduling | C: For Sched
AO3014 | Selected Schedule Point [2] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.2 | AI3016 | Scheduling | C: For Sched
AO3015 | Selected Schedule Point [2] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.2 | AI3017 | Scheduling | C: For Sched
AO3016 | Selected Schedule Point [2] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.2 | AI3018 | Scheduling | C: For Sched
AO3017 | Selected Schedule Point [2] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.2 | AI3019 | Scheduling | C: For Sched
AO3018 | Selected Schedule Point [3] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.3 | AI3020 | Scheduling | C: For Sched
AO3019 | Selected Schedule Point [3] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.3 | AI3021 | Scheduling | C: For Sched
AO3020 | Selected Schedule Point [3] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.3 | AI3022 | Scheduling | C: For Sched
AO3021 | Selected Schedule Point [3] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.3 | AI3023 | Scheduling | C: For Sched
AO3022 | Selected Schedule Point [4] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.4 | AI3024 | Scheduling | C: For Sched
AO3023 | Selected Schedule Point [4] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.4 | AI3025 | Scheduling | C: For Sched
AO3024 | Selected Schedule Point [4] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.4 | AI3026 | Scheduling | C: For Sched
AO3025 | Selected Schedule Point [4] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.4 | AI3027 | Scheduling | C: For Sched
AO3026 | Selected Schedule Point [5] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.5 | AI3028 | Scheduling | C: For Sched
AO3027 | Selected Schedule Point [5] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.5 | AI3029 | Scheduling | C: For Sched
AO3028 | Selected Schedule Point [5] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.5 | AI3030 | Scheduling | C: For Sched
AO3029 | Selected Schedule Point [5] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.5 | AI3031 | Scheduling | C: For Sched
AO3030 | Selected Schedule Point [6] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.6 | AI3032 | Scheduling | C: For Sched
AO3031 | Selected Schedule Point [6] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.6 | AI3033 | Scheduling | C: For Sched
AO3032 | Selected Schedule Point [6] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.6 | AI3034 | Scheduling | C: For Sched
AO3033 | Selected Schedule Point [6] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.6 | AI3035 | Scheduling | C: For Sched
AO3034 | Selected Schedule Point [7] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.7 | AI3036 | Scheduling | C: For Sched
AO3035 | Selected Schedule Point [7] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.7 | AI3037 | Scheduling | C: For Sched
AO3036 | Selected Schedule Point [7] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.7 | AI3038 | Scheduling | C: For Sched
AO3037 | Selected Schedule Point [7] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.7 | AI3039 | Scheduling | C: For Sched
AO3038 | Selected Schedule Point [8] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.8 | AI3040 | Scheduling | C: For Sched
AO3039 | Selected Schedule Point [8] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.8 | AI3041 | Scheduling | C: For Sched
AO3040 | Selected Schedule Point [8] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.8 | AI3042 | Scheduling | C: For Sched
AO3041 | Selected Schedule Point [8] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.8 | AI3043 | Scheduling | C: For Sched
AO3042 | Selected Schedule Point [9] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.9 | AI3044 | Scheduling | C: For Sched
AO3043 | Selected Schedule Point [9] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.9 | AI3045 | Scheduling | C: For Sched
AO3044 | Selected Schedule Point [9] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.9 | AI3046 | Scheduling | C: For Sched
AO3045 | Selected Schedule Point [9] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.9 | AI3047 | Scheduling | C: For Sched
AO3046 | Selected Schedule Point [10] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.10 | AI3048 | Scheduling | C: For Sched
AO3047 | Selected Schedule Point [10] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.10 | AI3049 | Scheduling | C: For Sched
AO3048 | Selected Schedule Point [10] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.10 | AI3050 | Scheduling | C: For Sched
AO3049 | Selected Schedule Point [10] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.10 | AI3051 | Scheduling | C: For Sched
AO3050 | Selected Schedule Point [11] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.11 | AI3052 | Scheduling | C: For Sched
AO3051 | Selected Schedule Point [11] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.11 | AI3053 | Scheduling | C: For Sched
AO3052 | Selected Schedule Point [11] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.11 | AI3054 | Scheduling | C: For Sched
AO3053 | Selected Schedule Point [11] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.11 | AI3055 | Scheduling | C: For Sched
AO3054 | Selected Schedule Point [12] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.12 | AI3056 | Scheduling | C: For Sched
AO3055 | Selected Schedule Point [12] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.12 | AI3057 | Scheduling | C: For Sched
AO3056 | Selected Schedule Point [12] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.12 | AI3058 | Scheduling | C: For Sched
AO3057 | Selected Schedule Point [12] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.12 | AI3059 | Scheduling | C: For Sched
AO3058 | Selected Schedule Point [13] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.13 | AI3060 | Scheduling | C: For Sched
AO3059 | Selected Schedule Point [13] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.13 | AI3061 | Scheduling | C: For Sched
AO3060 | Selected Schedule Point [13] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.13 | AI3062 | Scheduling | C: For Sched
AO3061 | Selected Schedule Point [13] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.13 | AI3063 | Scheduling | C: For Sched
AO3062 | Selected Schedule Point [14] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.14 | AI3064 | Scheduling | C: For Sched
AO3063 | Selected Schedule Point [14] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.14 | AI3065 | Scheduling | C: For Sched
AO3064 | Selected Schedule Point [14] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.14 | AI3066 | Scheduling | C: For Sched
AO3065 | Selected Schedule Point [14] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.14 | AI3067 | Scheduling | C: For Sched
AO3066 | Selected Schedule Point [15] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.15 | AI3068 | Scheduling | C: For Sched
AO3067 | Selected Schedule Point [15] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.15 | AI3069 | Scheduling | C: For Sched
AO3068 | Selected Schedule Point [15] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.15 | AI3070 | Scheduling | C: For Sched
AO3069 | Selected Schedule Point [15] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.15 | AI3071 | Scheduling | C: For Sched
AO3070 | Selected Schedule Point [16] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.16 | AI3072 | Scheduling | C: For Sched
AO3071 | Selected Schedule Point [16] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.16 | AI3073 | Scheduling | C: For Sched
AO3072 | Selected Schedule Point [16] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.16 | AI3074 | Scheduling | C: For Sched
AO3073 | Selected Schedule Point [16] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.16 | AI3075 | Scheduling | C: For Sched
AO3074 | Selected Schedule Point [17] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.17 | AI3076 | Scheduling | C: For Sched
AO3075 | Selected Schedule Point [17] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.17 | AI3077 | Scheduling | C: For Sched
AO3076 | Selected Schedule Point [17] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.17 | AI3078 | Scheduling | C: For Sched
AO3077 | Selected Schedule Point [17] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.17 | AI3079 | Scheduling | C: For Sched
AO3078 | Selected Schedule Point [18] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.18 | AI3080 | Scheduling | C: For Sched
AO3079 | Selected Schedule Point [18] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.18 | AI3081 | Scheduling | C: For Sched
AO3080 | Selected Schedule Point [18] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.18 | AI3082 | Scheduling | C: For Sched
AO3081 | Selected Schedule Point [18] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.18 | AI3083 | Scheduling | C: For Sched
AO3082 | Selected Schedule Point [19] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.19 | AI3084 | Scheduling | C: For Sched
AO3083 | Selected Schedule Point [19] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.19 | AI3085 | Scheduling | C: For Sched
AO3084 | Selected Schedule Point [19] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.19 | AI3086 | Scheduling | C: For Sched
AO3085 | Selected Schedule Point [19] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.19 | AI3087 | Scheduling | C: For Sched
AO3086 | Selected Schedule Point [20] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.20 | AI3088 | Scheduling | C: For Sched
AO3087 | Selected Schedule Point [20] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.20 | AI3089 | Scheduling | C: For Sched
AO3088 | Selected Schedule Point [20] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.20 | AI3090 | Scheduling | C: For Sched
AO3089 | Selected Schedule Point [20] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.20 | AI3091 | Scheduling | C: For Sched
AO3090 | Selected Schedule Point [21] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.21 | AI3092 | Scheduling
AO3091 | Selected Schedule Point [21] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.21 | AI3093 | Scheduling
AO3092 | Selected Schedule Point [21] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.21 | AI3094 | Scheduling
AO3093 | Selected Schedule Point [21] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.21 | AI3095 | Scheduling
AO3094 | Selected Schedule Point [22] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.22 | AI3096 | Scheduling
AO3095 | Selected Schedule Point [22] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.22 | AI3097 | Scheduling
AO3096 | Selected Schedule Point [22] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.22 | AI3098 | Scheduling
AO3097 | Selected Schedule Point [22] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.22 | AI3099 | Scheduling
AO3098 | Selected Schedule Point [23] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.23 | AI3100 | Scheduling
AO3099 | Selected Schedule Point [23] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.23 | AI3101 | Scheduling
AO3100 | Selected Schedule Point [23] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.23 | AI3102 | Scheduling
AO3101 | Selected Schedule Point [23] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.23 | AI3103 | Scheduling
AO3102 | Selected Schedule Point [24] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.24 | AI3104 | Scheduling
AO3103 | Selected Schedule Point [24] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.24 | AI3105 | Scheduling
AO3104 | Selected Schedule Point [24] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.24 | AI3106 | Scheduling
AO3105 | Selected Schedule Point [24] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.24 | AI3107 | Scheduling
AO3106 | Selected Schedule Point [25] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.25 | AI3108 | Scheduling
AO3107 | Selected Schedule Point [25] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.25 | AI3109 | Scheduling
AO3108 | Selected Schedule Point [25] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.25 | AI3110 | Scheduling
AO3109 | Selected Schedule Point [25] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.25 | AI3111 | Scheduling
AO3110 | Selected Schedule Point [26] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.26 | AI3112 | Scheduling
AO3111 | Selected Schedule Point [26] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.26 | AI3113 | Scheduling
AO3112 | Selected Schedule Point [26] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.26 | AI3114 | Scheduling
AO3113 | Selected Schedule Point [26] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.26 | AI3115 | Scheduling
AO3114 | Selected Schedule Point [27] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.27 | AI3116 | Scheduling
AO3115 | Selected Schedule Point [27] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.27 | AI3117 | Scheduling
AO3116 | Selected Schedule Point [27] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.27 | AI3118 | Scheduling
AO3117 | Selected Schedule Point [27] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.27 | AI3119 | Scheduling
AO3118 | Selected Schedule Point [28] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.28 | AI3120 | Scheduling
AO3119 | Selected Schedule Point [28] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.28 | AI3121 | Scheduling
AO3120 | Selected Schedule Point [28] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.28 | AI3122 | Scheduling
AO3121 | Selected Schedule Point [28] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.28 | AI3123 | Scheduling
AO3122 | Selected Schedule Point [29] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.29 | AI3124 | Scheduling
AO3123 | Selected Schedule Point [29] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.29 | AI3125 | Scheduling
AO3124 | Selected Schedule Point [29] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.29 | AI3126 | Scheduling
AO3125 | Selected Schedule Point [29] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.29 | AI3127 | Scheduling
AO3126 | Selected Schedule Point [30] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.30 | AI3128 | Scheduling
AO3127 | Selected Schedule Point [30] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.30 | AI3129 | Scheduling
AO3128 | Selected Schedule Point [30] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.30 | AI3130 | Scheduling
AO3129 | Selected Schedule Point [30] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.30 | AI3131 | Scheduling
AO3130 | Selected Schedule Point [31] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.31 | AI3132 | Scheduling
AO3131 | Selected Schedule Point [31] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.31 | AI3133 | Scheduling
AO3132 | Selected Schedule Point [31] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.31 | AI3134 | Scheduling
AO3133 | Selected Schedule Point [31] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.31 | AI3135 | Scheduling
AO3134 | Selected Schedule Point [32] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.32 | AI3136 | Scheduling
AO3135 | Selected Schedule Point [32] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.32 | AI3137 | Scheduling
AO3136 | Selected Schedule Point [32] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.32 | AI3138 | Scheduling
AO3137 | Selected Schedule Point [32] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.32 | AI3139 | Scheduling
AO3138 | Selected Schedule Point [33] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.33 | AI3140 | Scheduling
AO3139 | Selected Schedule Point [33] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.33 | AI3141 | Scheduling
AO3140 | Selected Schedule Point [33] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.33 | AI3142 | Scheduling
AO3141 | Selected Schedule Point [33] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.33 | AI3143 | Scheduling
AO3142 | Selected Schedule Point [34] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.34 | AI3144 | Scheduling
AO3143 | Selected Schedule Point [34] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.34 | AI3145 | Scheduling
AO3144 | Selected Schedule Point [34] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.34 | AI3146 | Scheduling
AO3145 | Selected Schedule Point [34] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.34 | AI3147 | Scheduling
AO3146 | Selected Schedule Point [35] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.35 | AI3148 | Scheduling
AO3147 | Selected Schedule Point [35] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.35 | AI3149 | Scheduling
AO3148 | Selected Schedule Point [35] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.35 | AI3150 | Scheduling
AO3149 | Selected Schedule Point [35] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.35 | AI3151 | Scheduling
AO3150 | Selected Schedule Point [36] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.36 | AI3152 | Scheduling
AO3151 | Selected Schedule Point [36] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.36 | AI3153 | Scheduling
AO3152 | Selected Schedule Point [36] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.36 | AI3154 | Scheduling
AO3153 | Selected Schedule Point [36] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.36 | AI3155 | Scheduling
AO3154 | Selected Schedule Point [37] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.37 | AI3156 | Scheduling
AO3155 | Selected Schedule Point [37] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.37 | AI3157 | Scheduling
AO3156 | Selected Schedule Point [37] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.37 | AI3158 | Scheduling
AO3157 | Selected Schedule Point [37] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.37 | AI3159 | Scheduling
AO3158 | Selected Schedule Point [38] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.38 | AI3160 | Scheduling
AO3159 | Selected Schedule Point [38] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.38 | AI3161 | Scheduling
AO3160 | Selected Schedule Point [38] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.38 | AI3162 | Scheduling
AO3161 | Selected Schedule Point [38] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.38 | AI3163 | Scheduling
AO3162 | Selected Schedule Point [39] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.39 | AI3164 | Scheduling
AO3163 | Selected Schedule Point [39] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.39 | AI3165 | Scheduling
AO3164 | Selected Schedule Point [39] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.39 | AI3166 | Scheduling
AO3165 | Selected Schedule Point [39] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.39 | AI3167 | Scheduling
AO3166 | Selected Schedule Point [40] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.40 | AI3168 | Scheduling
AO3167 | Selected Schedule Point [40] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.40 | AI3169 | Scheduling
AO3168 | Selected Schedule Point [40] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.40 | AI3170 | Scheduling
AO3169 | Selected Schedule Point [40] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.40 | AI3171 | Scheduling
AO3170 | Selected Schedule Point [41] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.41 | AI3172 | Scheduling
AO3171 | Selected Schedule Point [41] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.41 | AI3173 | Scheduling
AO3172 | Selected Schedule Point [41] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.41 | AI3174 | Scheduling
AO3173 | Selected Schedule Point [41] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.41 | AI3175 | Scheduling
AO3174 | Selected Schedule Point [42] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.42 | AI3176 | Scheduling
AO3175 | Selected Schedule Point [42] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.42 | AI3177 | Scheduling
AO3176 | Selected Schedule Point [42] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.42 | AI3178 | Scheduling
AO3177 | Selected Schedule Point [42] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.42 | AI3179 | Scheduling
AO3178 | Selected Schedule Point [43] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.43 | AI3180 | Scheduling
AO3179 | Selected Schedule Point [43] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.43 | AI3181 | Scheduling
AO3180 | Selected Schedule Point [43] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.43 | AI3182 | Scheduling
AO3181 | Selected Schedule Point [43] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.43 | AI3183 | Scheduling
AO3182 | Selected Schedule Point [44] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.44 | AI3184 | Scheduling
AO3183 | Selected Schedule Point [44] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.44 | AI3185 | Scheduling
AO3184 | Selected Schedule Point [44] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.44 | AI3186 | Scheduling
AO3185 | Selected Schedule Point [44] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.44 | AI3187 | Scheduling
AO3186 | Selected Schedule Point [45] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.45 | AI3188 | Scheduling
AO3187 | Selected Schedule Point [45] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.45 | AI3189 | Scheduling
AO3188 | Selected Schedule Point [45] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.45 | AI3190 | Scheduling
AO3189 | Selected Schedule Point [45] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.45 | AI3191 | Scheduling
AO3190 | Selected Schedule Point [46] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.46 | AI3192 | Scheduling
AO3191 | Selected Schedule Point [46] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.46 | AI3193 | Scheduling
AO3192 | Selected Schedule Point [46] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.46 | AI3194 | Scheduling
AO3193 | Selected Schedule Point [46] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.46 | AI3195 | Scheduling
AO3194 | Selected Schedule Point [47] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.47 | AI3196 | Scheduling
AO3195 | Selected Schedule Point [47] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.47 | AI3197 | Scheduling
AO3196 | Selected Schedule Point [47] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.47 | AI3198 | Scheduling
AO3197 | Selected Schedule Point [47] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.47 | AI3199 | Scheduling
AO3198 | Selected Schedule Point [48] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.48 | AI3200 | Scheduling
AO3199 | Selected Schedule Point [48] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.48 | AI3201 | Scheduling
AO3200 | Selected Schedule Point [48] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.48 | AI3202 | Scheduling
AO3201 | Selected Schedule Point [48] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.48 | AI3203 | Scheduling
AO3202 | Selected Schedule Point [49] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.49 | AI3204 | Scheduling
AO3203 | Selected Schedule Point [49] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.49 | AI3205 | Scheduling
AO3204 | Selected Schedule Point [49] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.49 | AI3206 | Scheduling
AO3205 | Selected Schedule Point [49] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.49 | AI3207 | Scheduling
AO3206 | Selected Schedule Point [50] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.50 | AI3208 | Scheduling
AO3207 | Selected Schedule Point [50] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.50 | AI3209 | Scheduling
AO3208 | Selected Schedule Point [50] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.50 | AI3210 | Scheduling
AO3209 | Selected Schedule Point [50] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.50 | AI3211 | Scheduling
AO3210 | Selected Schedule Point [51] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.51 | AI3212 | Scheduling
AO3211 | Selected Schedule Point [51] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.51 | AI3213 | Scheduling
AO3212 | Selected Schedule Point [51] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.51 | AI3214 | Scheduling
AO3213 | Selected Schedule Point [51] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.51 | AI3215 | Scheduling
AO3214 | Selected Schedule Point [52] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.52 | AI3216 | Scheduling
AO3215 | Selected Schedule Point [52] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.52 | AI3217 | Scheduling
AO3216 | Selected Schedule Point [52] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.52 | AI3218 | Scheduling
AO3217 | Selected Schedule Point [52] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.52 | AI3219 | Scheduling
AO3218 | Selected Schedule Point [53] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.53 | AI3220 | Scheduling
AO3219 | Selected Schedule Point [53] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.53 | AI3221 | Scheduling
AO3220 | Selected Schedule Point [53] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.53 | AI3222 | Scheduling
AO3221 | Selected Schedule Point [53] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.53 | AI3223 | Scheduling
AO3222 | Selected Schedule Point [54] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.54 | AI3224 | Scheduling
AO3223 | Selected Schedule Point [54] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.54 | AI3225 | Scheduling
AO3224 | Selected Schedule Point [54] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.54 | AI3226 | Scheduling
AO3225 | Selected Schedule Point [54] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.54 | AI3227 | Scheduling
AO3226 | Selected Schedule Point [55] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.55 | AI3228 | Scheduling
AO3227 | Selected Schedule Point [55] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.55 | AI3229 | Scheduling
AO3228 | Selected Schedule Point [55] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.55 | AI3230 | Scheduling
AO3229 | Selected Schedule Point [55] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.55 | AI3231 | Scheduling
AO3230 | Selected Schedule Point [56] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.56 | AI3232 | Scheduling
AO3231 | Selected Schedule Point [56] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.56 | AI3233 | Scheduling
AO3232 | Selected Schedule Point [56] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.56 | AI3234 | Scheduling
AO3233 | Selected Schedule Point [56] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.56 | AI3235 | Scheduling
AO3234 | Selected Schedule Point [57] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.57 | AI3236 | Scheduling
AO3235 | Selected Schedule Point [57] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.57 | AI3237 | Scheduling
AO3236 | Selected Schedule Point [57] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.57 | AI3238 | Scheduling
AO3237 | Selected Schedule Point [57] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.57 | AI3239 | Scheduling
AO3238 | Selected Schedule Point [58] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.58 | AI3240 | Scheduling
AO3239 | Selected Schedule Point [58] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.58 | AI3241 | Scheduling
AO3240 | Selected Schedule Point [58] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.58 | AI3242 | Scheduling
AO3241 | Selected Schedule Point [58] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.58 | AI3243 | Scheduling
AO3242 | Selected Schedule Point [59] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.59 | AI3244 | Scheduling
AO3243 | Selected Schedule Point [59] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.59 | AI3245 | Scheduling
AO3244 | Selected Schedule Point [59] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.59 | AI3246 | Scheduling
AO3245 | Selected Schedule Point [59] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.59 | AI3247 | Scheduling
AO3246 | Selected Schedule Point [60] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.60 | AI3248 | Scheduling
AO3247 | Selected Schedule Point [60] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.60 | AI3249 | Scheduling
AO3248 | Selected Schedule Point [60] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.60 | AI3250 | Scheduling
AO3249 | Selected Schedule Point [60] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.60 | AI3251 | Scheduling
AO3250 | Selected Schedule Point [61] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.61 | AI3252 | Scheduling
AO3251 | Selected Schedule Point [61] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.61 | AI3253 | Scheduling
AO3252 | Selected Schedule Point [61] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.61 | AI3254 | Scheduling
AO3253 | Selected Schedule Point [61] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.61 | AI3255 | Scheduling
AO3254 | Selected Schedule Point [62] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.62 | AI3256 | Scheduling
AO3255 | Selected Schedule Point [62] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.62 | AI3257 | Scheduling
AO3256 | Selected Schedule Point [62] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.62 | AI3258 | Scheduling
AO3257 | Selected Schedule Point [62] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.62 | AI3259 | Scheduling
AO3258 | Selected Schedule Point [63] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.63 | AI3260 | Scheduling
AO3259 | Selected Schedule Point [63] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.63 | AI3261 | Scheduling
AO3260 | Selected Schedule Point [63] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.63 | AI3262 | Scheduling
AO3261 | Selected Schedule Point [63] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.63 | AI3263 | Scheduling
AO3262 | Selected Schedule Point [64] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.64 | AI3264 | Scheduling
AO3263 | Selected Schedule Point [64] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.64 | AI3265 | Scheduling
AO3264 | Selected Schedule Point [64] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.64 | AI3266 | Scheduling
AO3265 | Selected Schedule Point [64] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.64 | AI3267 | Scheduling
AO3266 | Selected Schedule Point [65] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.65 | AI3268 | Scheduling
AO3267 | Selected Schedule Point [65] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.65 | AI3269 | Scheduling
AO3268 | Selected Schedule Point [65] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.65 | AI3270 | Scheduling
AO3269 | Selected Schedule Point [65] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.65 | AI3271 | Scheduling
AO3270 | Selected Schedule Point [66] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.66 | AI3272 | Scheduling
AO3271 | Selected Schedule Point [66] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.66 | AI3273 | Scheduling
AO3272 | Selected Schedule Point [66] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.66 | AI3274 | Scheduling
AO3273 | Selected Schedule Point [66] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.66 | AI3275 | Scheduling
AO3274 | Selected Schedule Point [67] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.67 | AI3276 | Scheduling
AO3275 | Selected Schedule Point [67] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.67 | AI3277 | Scheduling
AO3276 | Selected Schedule Point [67] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.67 | AI3278 | Scheduling
AO3277 | Selected Schedule Point [67] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.67 | AI3279 | Scheduling
AO3278 | Selected Schedule Point [68] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.68 | AI3280 | Scheduling
AO3279 | Selected Schedule Point [68] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.68 | AI3281 | Scheduling
AO3280 | Selected Schedule Point [68] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.68 | AI3282 | Scheduling
AO3281 | Selected Schedule Point [68] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.68 | AI3283 | Scheduling
AO3282 | Selected Schedule Point [69] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.69 | AI3284 | Scheduling
AO3283 | Selected Schedule Point [69] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.69 | AI3285 | Scheduling
AO3284 | Selected Schedule Point [69] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.69 | AI3286 | Scheduling
AO3285 | Selected Schedule Point [69] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.69 | AI3287 | Scheduling
AO3286 | Selected Schedule Point [70] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.70 | AI3288 | Scheduling
AO3287 | Selected Schedule Point [70] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.70 | AI3289 | Scheduling
AO3288 | Selected Schedule Point [70] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.70 | AI3290 | Scheduling
AO3289 | Selected Schedule Point [70] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.70 | AI3291 | Scheduling
AO3290 | Selected Schedule Point [71] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.71 | AI3292 | Scheduling
AO3291 | Selected Schedule Point [71] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.71 | AI3293 | Scheduling
AO3292 | Selected Schedule Point [71] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.71 | AI3294 | Scheduling
AO3293 | Selected Schedule Point [71] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.71 | AI3295 | Scheduling
AO3294 | Selected Schedule Point [72] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.72 | AI3296 | Scheduling
AO3295 | Selected Schedule Point [72] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.72 | AI3297 | Scheduling
AO3296 | Selected Schedule Point [72] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.72 | AI3298 | Scheduling
AO3297 | Selected Schedule Point [72] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.72 | AI3299 | Scheduling
AO3298 | Selected Schedule Point [73] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.73 | AI3300 | Scheduling
AO3299 | Selected Schedule Point [73] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.73 | AI3301 | Scheduling
AO3300 | Selected Schedule Point [73] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.73 | AI3302 | Scheduling
AO3301 | Selected Schedule Point [73] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.73 | AI3303 | Scheduling
AO3302 | Selected Schedule Point [74] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.74 | AI3304 | Scheduling
AO3303 | Selected Schedule Point [74] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.74 | AI3305 | Scheduling
AO3304 | Selected Schedule Point [74] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.74 | AI3306 | Scheduling
AO3305 | Selected Schedule Point [74] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.74 | AI3307 | Scheduling
AO3306 | Selected Schedule Point [75] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.75 | AI3308 | Scheduling
AO3307 | Selected Schedule Point [75] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.75 | AI3309 | Scheduling
AO3308 | Selected Schedule Point [75] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.75 | AI3310 | Scheduling
AO3309 | Selected Schedule Point [75] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.75 | AI3311 | Scheduling
AO3310 | Selected Schedule Point [76] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.76 | AI3312 | Scheduling
AO3311 | Selected Schedule Point [76] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.76 | AI3313 | Scheduling
AO3312 | Selected Schedule Point [76] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.76 | AI3314 | Scheduling
AO3313 | Selected Schedule Point [76] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.76 | AI3315 | Scheduling
AO3314 | Selected Schedule Point [77] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.77 | AI3316 | Scheduling
AO3315 | Selected Schedule Point [77] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.77 | AI3317 | Scheduling
AO3316 | Selected Schedule Point [77] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.77 | AI3318 | Scheduling
AO3317 | Selected Schedule Point [77] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.77 | AI3319 | Scheduling
AO3318 | Selected Schedule Point [78] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.78 | AI3320 | Scheduling
AO3319 | Selected Schedule Point [78] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.78 | AI3321 | Scheduling
AO3320 | Selected Schedule Point [78] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.78 | AI3322 | Scheduling
AO3321 | Selected Schedule Point [78] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.78 | AI3323 | Scheduling
AO3322 | Selected Schedule Point [79] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.79 | AI3324 | Scheduling
AO3323 | Selected Schedule Point [79] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.79 | AI3325 | Scheduling
AO3324 | Selected Schedule Point [79] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.79 | AI3326 | Scheduling
AO3325 | Selected Schedule Point [79] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.79 | AI3327 | Scheduling
AO3326 | Selected Schedule Point [80] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.80 | AI3328 | Scheduling
AO3327 | Selected Schedule Point [80] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.80 | AI3329 | Scheduling
AO3328 | Selected Schedule Point [80] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.80 | AI3330 | Scheduling
AO3329 | Selected Schedule Point [80] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.80 | AI3331 | Scheduling
AO3330 | Selected Schedule Point [81] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.81 | AI3332 | Scheduling
AO3331 | Selected Schedule Point [81] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.81 | AI3333 | Scheduling
AO3332 | Selected Schedule Point [81] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.81 | AI3334 | Scheduling
AO3333 | Selected Schedule Point [81] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.81 | AI3335 | Scheduling
AO3334 | Selected Schedule Point [82] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.82 | AI3336 | Scheduling
AO3335 | Selected Schedule Point [82] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.82 | AI3337 | Scheduling
AO3336 | Selected Schedule Point [82] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.82 | AI3338 | Scheduling
AO3337 | Selected Schedule Point [82] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.82 | AI3339 | Scheduling
AO3338 | Selected Schedule Point [83] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.83 | AI3340 | Scheduling
AO3339 | Selected Schedule Point [83] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.83 | AI3341 | Scheduling
AO3340 | Selected Schedule Point [83] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.83 | AI3342 | Scheduling
AO3341 | Selected Schedule Point [83] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.83 | AI3343 | Scheduling
AO3342 | Selected Schedule Point [84] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.84 | AI3344 | Scheduling
AO3343 | Selected Schedule Point [84] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.84 | AI3345 | Scheduling
AO3344 | Selected Schedule Point [84] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.84 | AI3346 | Scheduling
AO3345 | Selected Schedule Point [84] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.84 | AI3347 | Scheduling
AO3346 | Selected Schedule Point [85] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.85 | AI3348 | Scheduling
AO3347 | Selected Schedule Point [85] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.85 | AI3349 | Scheduling
AO3348 | Selected Schedule Point [85] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.85 | AI3350 | Scheduling
AO3349 | Selected Schedule Point [85] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.85 | AI3351 | Scheduling
AO3350 | Selected Schedule Point [86] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.86 | AI3352 | Scheduling
AO3351 | Selected Schedule Point [86] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.86 | AI3353 | Scheduling
AO3352 | Selected Schedule Point [86] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.86 | AI3354 | Scheduling
AO3353 | Selected Schedule Point [86] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.86 | AI3355 | Scheduling
AO3354 | Selected Schedule Point [87] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.87 | AI3356 | Scheduling
AO3355 | Selected Schedule Point [87] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.87 | AI3357 | Scheduling
AO3356 | Selected Schedule Point [87] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.87 | AI3358 | Scheduling
AO3357 | Selected Schedule Point [87] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.87 | AI3359 | Scheduling
AO3358 | Selected Schedule Point [88] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.88 | AI3360 | Scheduling
AO3359 | Selected Schedule Point [88] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.88 | AI3361 | Scheduling
AO3360 | Selected Schedule Point [88] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.88 | AI3362 | Scheduling
AO3361 | Selected Schedule Point [88] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.88 | AI3363 | Scheduling
AO3362 | Selected Schedule Point [89] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.89 | AI3364 | Scheduling
AO3363 | Selected Schedule Point [89] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.89 | AI3365 | Scheduling
AO3364 | Selected Schedule Point [89] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.89 | AI3366 | Scheduling
AO3365 | Selected Schedule Point [89] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.89 | AI3367 | Scheduling
AO3366 | Selected Schedule Point [90] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.90 | AI3368 | Scheduling
AO3367 | Selected Schedule Point [90] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.90 | AI3369 | Scheduling
AO3368 | Selected Schedule Point [90] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.90 | AI3370 | Scheduling
AO3369 | Selected Schedule Point [90] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.90 | AI3371 | Scheduling
AO3370 | Selected Schedule Point [91] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.91 | AI3372 | Scheduling
AO3371 | Selected Schedule Point [91] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.91 | AI3373 | Scheduling
AO3372 | Selected Schedule Point [91] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.91 | AI3374 | Scheduling
AO3373 | Selected Schedule Point [91] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.91 | AI3375 | Scheduling
AO3374 | Selected Schedule Point [92] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.92 | AI3376 | Scheduling
AO3375 | Selected Schedule Point [92] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.92 | AI3377 | Scheduling
AO3376 | Selected Schedule Point [92] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.92 | AI3378 | Scheduling
AO3377 | Selected Schedule Point [92] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.92 | AI3379 | Scheduling
AO3378 | Selected Schedule Point [93] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.93 | AI3380 | Scheduling
AO3379 | Selected Schedule Point [93] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.93 | AI3381 | Scheduling
AO3380 | Selected Schedule Point [93] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.93 | AI3382 | Scheduling
AO3381 | Selected Schedule Point [93] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.93 | AI3383 | Scheduling
AO3382 | Selected Schedule Point [94] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.94 | AI3384 | Scheduling
AO3383 | Selected Schedule Point [94] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.94 | AI3385 | Scheduling
AO3384 | Selected Schedule Point [94] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.94 | AI3386 | Scheduling
AO3385 | Selected Schedule Point [94] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.94 | AI3387 | Scheduling
AO3386 | Selected Schedule Point [95] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.95 | AI3388 | Scheduling
AO3387 | Selected Schedule Point [95] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.95 | AI3389 | Scheduling
AO3388 | Selected Schedule Point [95] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.95 | AI3390 | Scheduling
AO3389 | Selected Schedule Point [95] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.95 | AI3391 | Scheduling
AO3390 | Selected Schedule Point [96] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.96 | AI3392 | Scheduling
AO3391 | Selected Schedule Point [96] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.96 | AI3393 | Scheduling
AO3392 | Selected Schedule Point [96] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.96 | AI3394 | Scheduling
AO3393 | Selected Schedule Point [96] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.96 | AI3395 | Scheduling
AO3394 | Selected Schedule Point [97] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.97 | AI3396 | Scheduling
AO3395 | Selected Schedule Point [97] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.97 | AI3397 | Scheduling
AO3396 | Selected Schedule Point [97] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.97 | AI3398 | Scheduling
AO3397 | Selected Schedule Point [97] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.97 | AI3399 | Scheduling
AO3398 | Selected Schedule Point [98] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.98 | AI3400 | Scheduling
AO3399 | Selected Schedule Point [98] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.98 | AI3401 | Scheduling
AO3400 | Selected Schedule Point [98] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.98 | AI3402 | Scheduling
AO3401 | Selected Schedule Point [98] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.98 | AI3403 | Scheduling
AO3402 | Selected Schedule Point [99] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.99 | AI3404 | Scheduling
AO3403 | Selected Schedule Point [99] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.99 | AI3405 | Scheduling
AO3404 | Selected Schedule Point [99] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.99 | AI3406 | Scheduling
AO3405 | Selected Schedule Point [99] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.99 | AI3407 | Scheduling
AO3406 | Selected Schedule Point [100] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.100 | AI3408 | Scheduling
AO3407 | Selected Schedule Point [100] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.100 | AI3409 | Scheduling
AO3408 | Selected Schedule Point [100] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.100 | AI3410 | Scheduling
AO3409 | Selected Schedule Point [100] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.100 | AI3411 | Scheduling
AO5000 | Meter #1 Active Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.hLim | AI5025 | Equipment Data
AO5001 | Meter #1 Active Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.lLim | AI5026 | Equipment Data
AO5002 | Meter #1 Reactive Power – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.hLim | AI5027 | Equipment Data
AO5003 | Meter #1 at Reactive Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.lLim | AI5028 | Equipment Data
AO5004 | Meter #1 at Power Factor – High Threshold | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.hLim | AI5029 | Equipment Data
AO5005 | Meter #1 at Power Factor – Low Threshold | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.lLim | AI5030 | Equipment Data
AO5006 | Meter #1 Phase A Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.hLim | AI5031 | Equipment Data
AO5007 | Meter #1 Phase A Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.lLim | AI5032 | Equipment Data
AO5008 | Meter #1 Phase B Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.hLim | AI5033 | Equipment Data
AO5009 | Meter #1 Phase B Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.lLim | AI5034 | Equipment Data
AO5010 | Meter #1 Phase C Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.hLim | AI5035 | Equipment Data
AO5011 | Meter #1 Phase C Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.lLim | AI5036 | Equipment Data
AO15000 | Inverter #1 Active Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.hLim | AI15021 | Equipment Data
AO15001 | Inverter #1 Active Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.lLim | AI15022 | Equipment Data
AO15002 | Inverter #1 Reactive Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.hLim | AI15023 | Equipment Data
AO15003 | Inverter #1 Reactive Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.lLim | AI15024 | Equipment Data
AO15004 | Inverter #1 Current Output Frequency – High Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.hLim | AI15025 | Equipment Data
AO15005 | Inverter #1 Current Output Frequency – Low Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.lLim | AI15026 | Equipment Data
AO15006 | Inverter #1 DC Inverter Input Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.hLim | AI15027 | Equipment Data
AO15007 | Inverter #1 DC Inverter Input Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.lLim | AI15028 | Equipment Data
AO15008 | Inverter #1 DC Current Available – High Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter1.MMDC.Amp.RangeC.hLim | AI15029 | Equipment Data
AO15009 | Inverter #1 DC Current Available – Low Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter1.MMDC.Amp.RangeC.lLim | AI15030 | Equipment Data
AO15010 | Inverter #1 DC Voltage Between DER System and Inverter – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.hLim | AI15031 | Equipment Data
AO15011 | Inverter #1 DC Voltage Between DER System and Inverter – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.lLim | AI15032 | Equipment Data
AO15024 | Inverter #3 Active Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMXU.TotW.RangeC.hLim | AI15089 | Equipment Data
AO15025 | Inverter #3 Active Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMXU.TotW.RangeC.lLim | AI15090 | Equipment Data
AO15026 | Inverter #3 Reactive Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter3.MMXU.TotVAr.rangeC.hLim | AI15091 | Equipment Data
AO15027 | Inverter #3 Reactive Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter3.MMXU.TotVAr.rangeC.lLim | AI15092 | Equipment Data
AO15028 | Inverter #3 Current Output Frequency – High Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter3.MMXU.Hz.rangeC.hLim | AI15093 | Equipment Data
AO15029 | Inverter #3 Current Output Frequency – Low Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter3.MMXU.Hz.rangeC.lLim | AI15094 | Equipment Data
AO15030 | Inverter #3 DC Inverter Input Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMDC.Watt.RangeC.hLim | AI15095 | Equipment Data
AO15031 | Inverter #3 DC Inverter Input Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMDC.Watt.RangeC.lLim | AI15096 | Equipment Data
AO15032 | Inverter #3 DC Input Current Available – High Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter3.MMDC.Amp.RangeC.hLim | AI15097 | Equipment Data
AO15033 | Inverter #3 DC Input Current Available – Low Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter3.MMDC.Amp.RangeC.lLim | AI15098 | Equipment Data
AO15034 | Inverter #3 DC Voltage Between DER System and Inverter – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMDC.Vol.RangeC.hLim | AI15099 | Equipment Data
AO15035 | Inverter #3 DC Voltage Between DER System and Inverter – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMDC.Vol.RangeC.lLim | AI15100 | Equipment Data
AO20000 | Battery Bank #1 External Voltage - High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolHiAls | AI20023 | Equipment Data
AO20001 | Battery Bank #1 External Voltage - Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolLoAls | AI20024 | Equipment Data
AO20002 | Battery Bank #1 Internal Voltage – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolHiAls | AI20025 | Equipment Data
AO20003 | Battery Bank #1 Internal Voltage – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolLoAls | AI20026 | Equipment Data
AO20008 | Battery Bank #3 External Voltage - High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.ExtVolHiAls | AO20008 | Equipment Data
AO20009 | Battery Bank #3 External Voltage - Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.ExtVolLoAls | AO20009 | Equipment Data
AO20010 | Battery Bank #3 Internal Voltage – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.IntnVolHiAls | AO20010 | Equipment Data
AO20011 | Battery Bank #3 Internal Voltage – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.IntnVolLoAls | AO20011 | Equipment Data
AO30000 | Volt-Watt Adv Mode Priority | 0 | 100 | 1 | 0 | n/a | DVWC1.ModPrio | AI30000 | Volt-Watt Advanced
AO30001 | Volt-Watt Adv Enabling Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.WinTms | AI30001 | Volt-Watt Advanced
AO30002 | Volt-Watt Adv Enabling Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.RmpTms | AI30002 | Volt-Watt Advanced
AO30003 | Volt-Watt Adv Reversion Timeout Period | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.RvrtTms | AI30003 | Volt-Watt Advanced
AO30004 | Volt-Watt Adv Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | AI30004 | Volt-Watt Advanced | C: For Function
AO30005 | Volt-Watt Adv High Start Voltage Threshold. Voltage threshold for starting high voltage events. | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | AI30006 | Volt-Watt Advanced | C: For Function
AO30006 | Volt-Watt Adv High Stop Voltage Threshold. Voltage threshold for stopping high voltage events. | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStop | AI30007 | Volt-Watt Advanced
AO30007 | Volt-Watt Adv Low Start Voltage Threshold. Voltage threshold for starting low voltage events. | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | AI30008 | Volt-Watt Advanced | C: For Function
AO30008 | Volt-Watt Adv Low Stop Voltage Threshold. Voltage threshold for stopping low voltage events. | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStop | AI30009 | Volt-Watt Advanced
AO30009 | Volt-Watt Adv Start Delay. Delay at start thresholds to verify voltage exceeds that threshold. | 0 | 2147483647 | 1 | 0 | milliseconds | DVWC1.ActStrDlTmms | AI30010 | Volt-Watt Advanced
AO30010 | Volt-Watt Adv Stop Delay. Delay at stop thresholds to verify voltage has returned to normal. | 0 | 2147483647 | 1 | 0 | milliseconds | DVWC1.ActStopDlTmms | AI30011 | Volt-Watt Advanced
AO30011 | Volt-Watt Adv Curve Index. Index of the Volt-Watt Adv curve that should be used by the m | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | AI30012 | Volt-Watt Advanced | C: For Function
AO30012 | Volt-Watt Adv Filter Time (Seconds) | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.FilTms | AI30014 | Volt-Watt Advanced
AO30013 | Volt-Watt Adv Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.1 | AI30015 | Volt-Watt Advanced
AO30014 | Volt-Watt Adv Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.2 | AI30016 | Volt-Watt Advanced
AO30015 | Volt-Watt Adv Discharging Ramp Up Rate. Maximum ramp up rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuRte | AI30017 | Volt-Watt Advanced | C: For Function
AO30016 | Volt-Watt Adv Discharging Ramp Down Rate. Maximum ramp down rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdRte | AI30018 | Volt-Watt Advanced | C: For Function
AO30017 | Volt-Watt Adv Charging Ramp Up Rate. Maximum charging ramp up rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuChaRte | AI30019 | Volt-Watt Advanced | C: For Function
AO30018 | Volt-Watt Adv Charging Ramp Down Rate. Maximum charging ramp down rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdChaRte | AI30020 | Volt-Watt Advanced | C: For Function
AO30019 | Volt-Watt Adv Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMinPct | AI30021 | Volt-Watt Advanced | C: For Function
AO30020 | Volt-Watt Adv Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMaxPct | AI30022 | Volt-Watt Advanced | C: For Function
AO30050 | Synthetic Inertia Priority | 0 | 100 | 1 | 0 | n/a | DSYN.ModPrio | AI30050 | Synthetic Inertia
AO30051 | Synthetic Inertia Time Window | 0 | 2147483647 | 1 | 0 | Seconds | DSYN.WinTms | AI30051 | Synthetic Inertia
AO30052 | Synthetic Inertia Ramp Time | 0 | 2147483647 | 1 | 0 | Seconds | DSYN.RmpTms | AI30052 | Synthetic Inertia
AO30053 | Synthetic Inertia Reversion Timeout | 0 | 2147483647 | 1 | 0 | Seconds | DSYN.RvrtTms | AI30053 | Synthetic Inertia
AO30054 | Synthetic Inertia Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DSYN.EcpRef | AI30054 | Synthetic Inertia
AO30055 | Set the Synthetic Inertia Discharge Ramp Up Rate | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.DschRpuPct | AI30055 | Synthetic Inertia
AO30056 | Set the Synthetic Inertia Discharge Ramp Down Rate | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.DschRpdPct | AI30056 | Synthetic Inertia
AO30057 | Set the Synthetic Inertia Charge Ramp Up Rate | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.ChaRpuPct | AI30057 | Synthetic Inertia
AO30058 | Set the Synthetic Inertia Charge Ramp Down Rate | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.ChaRpdPct | AI30058 | Synthetic Inertia
AO30059 | Set the Synthetic Inertia Derivative Factor | 0 | 2147483647 | 1 | 0 | Percent W per Hz per sec | DSYN.RcfWHzTmPct | AI30059 | Synthetic Inertia
AO30060 | Set the Synthetic Inertia Lower Deadband | 0 | 2147483647 | 1 | 0 | Hz | DSYN.DbHzMin | AI30060 | Synthetic Inertia
AO30061 | Set the Synthetic Inertia Upper Deadband | 0 | 2147483647 | 1 | 0 | Hz | DSYN.DbHzMax | AI30061 | Synthetic Inertia
VP | Vendor Points

## AI
DNP3 Point Index | Name / Description | Default Event Class | Transmitted Value |  | Scaling |  | Units | IEC61850 | Additional Information |  |  |  |  | EUT Capabilities
|  |  | Minimum | Maximum | Multiplier | Offset |  | IEC61850UniqueString | Value | Assoc. AO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AI0 | DER Profile Version Number. | 3 | 100 | 10000 | 0.01 | 0 | n/a | MESA.VersNum | 1.1 |  | Nameplate | M
AI1 | DER Profile Implementation Level. 1, 2 or 3 to indicate support for Level 1, Level 2 or Level 3 respectively. 0 means ignore | 3 | 0 | 3 | 1 | 0 | n/a | MESA.ImplLvl | 0 |  | Nameplate | M
AI2 | Nameplate Minimum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMinRtg | 0 |  | Nameplate | M | M
AI3 | Nameplate Maximum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMaxRtg | 0 |  | Nameplate | M | M
AI4 | Nameplate Active Generation Power Rating at Unity Power Factor | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMaxRtg | 0 |  | Nameplate | M | M
AI5 | Nameplate Active Charging Power Rating at Unity Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWMaxRtg | 0 |  | Nameplate | C: For Storage
AI6 | Nameplate Active Generation Power Rating at Specified Over-Excited Power Factor, injecting reactive power (as positive vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WOvPFRtg | 0 |  | Nameplate | M | M
AI7 | Nameplate Active Charging Power Rating at Specified Over-Excited Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWOvPFRtg | 0 |  | Nameplate | C: For Storage
AI8 | Specified Over-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.OvPFRtg | 0 |  | Nameplate | M | M
AI9 | Nameplate Active Generation Power Rating at Specified Under-Excited Power Factor, absorbing reactive power (as negative vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WUnPFRtg | 0 |  | Nameplate | M | M
AI10 | Nameplate Active Charging Power Rating at Specified Under-Excited Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWUnPFRtg | 0 |  | Nameplate | M | M
AI11 | Specified Under-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.UnPFRtg | 0 |  | Nameplate | M | M
AI12 | Nameplate Reactive Supply (Injection) Power Rating | 3 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMaxRtg | 0 |  | Nameplate | M | M
AI13 | Nameplate Reactive Absorption Power Rating | 3 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMaxRtg | 0 |  | Nameplate | M | M
AI14 | Nameplate Apparent Generation Power Rating | 3 | 0 | 2147483647 | 1 | 0 | VAs | DGEN.VAMaxRtg | 0 |  | Nameplate | M
AI15 | Nameplate Apparent Charging Power Rating | 3 | -2147483648 | 0 | 1 | 0 | VAs | DSTO.ChaVAMaxRtg | 0 |  | Nameplate | M | M
AI16 | Nameplate Storage Actual Energy Capacity. Nameplate (original) actual total energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.WhRtg | 0 |  | Nameplate | C: For Storage | M
AI17 | Storage Effective Actual Energy Capacity. Present actual total energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.EffWh | 0 |  | Nameplate | C: For Storage
AI18 | Storage Usable Energy Capacity. Usable energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.UseWh | 0 |  | Nameplate | C: For Storage
AI19 | Nameplate AC Current Maximum Generation Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Amps | DGEN.AMaxRtg | 0 |  | Nameplate | M
AI20 | Nameplate AC Current Maximum Charging Rating | 3 | -2147483648 | 0 | 0.1 | 0 | Amps | DSTO.ChaAMaxRtg | 0 |  | Nameplate | C: For Storage
AI21 | Remaining Reactive Susceptance | 3 | -2147483648 | 2147483647 | 1 | 0 | Siemens | DGEN.SuscRtg | 0 |  | Nameplate |  | M
AI22 | IEEE 1547 Normal Operating Performance Category. Enumeration: <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DGEN.RegClas.1 | 0 |  | Nameplate | M | M
AI23 | IEEE 1547 Abnormal Operating Performance Category. Enumeration: <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DGEN.RegClas.2 | 0 |  | Nameplate | M | M
AI24 | Number of System Schedules | 3 | 0 | 100 | 1 | 0 | None | MESA.NumSchd | 0 |  | Config | M
AI25 | Number of Meters | 3 | 0 | 3 | 1 | 0 | None | MESA.NumMtr | 3 |  | Config | M
AI26 | Number of Inverters | 3 | 0 | 2 | 1 | 0 | None | MESA.NumInv | 2 |  | Config | M
AI27 | Number of Batteries | 3 | 0 | 2 | 1 | 0 | None | MESA.NumBat | 2 |  | Config | M
AI28 | Number of DER units connected to controller | 3 | 0 | 7 | 1 | 0 | None | DSTO.InclDER | 7 |  | Config | M
AI29 | Reference Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VRef | 0 | AO0 | Config | M | M
AI30 | Reference Voltage Offset | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts | DECP.VRefOfs | 0 | AO1 | Config | M | M
AI31 | Nominal Grid Frequency | 2 | 0 | 70000 | 0.001 | 0 | Hz | DECP.EcpHzNom | 0 | AO2 | Config | M
AI32 | Maximum Active Generation Power | 2 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMax | 0 |  | Operational Settings | M | M
AI33 | Maximum Active Charging Power | 2 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWMax | 0 |  | Operational Settings | C: For Storage
AI34 | Maximum Reactive Injection Power | 2 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMax | 0 |  | Operational Settings | M | M
AI35 | Maximum Reactive Absorption Power | 2 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMax | 0 |  | Operational Settings | M | M
AI36 | Maximum Apparent Generation Power | 2 | 0 | 2147483647 | 1 | 0 | VA | DGEN.VAMax | 0 |  | Operational Settings | M
AI37 | Maximum Apparent Charging Power | 2 | -2147483648 | 0 | 1 | 0 | VA | DSTO.ChaVAMax | 0 |  | Operational Settings | C: For Storage
AI38 | Minimum Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VMin | 0 |  | Operational Settings | M
AI39 | Maximum Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VMax | 0 |  | Operational Settings | M
AI40 | Open Loop Response Time Percentage. Percent of target to reach witInvertern the open loop response time. Default is 90%. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DGEN.OplPct | 0 |  | Operational Settings | M
AI41 | Power Factor Sign Convention. Enumeration: <1> IEC – active power <2> IEEE – lead/lag | 2 | 1 | 2 | 1 | 0 | None | PF.MMXU.PFSign | 1 | AO4 | Operational Settings | M
AI42 | Reference for Reactive Power Setpoints. Selects which setpoint is active. Default is <3>. <0> Not applicable / Unknown <1> Percent of Maximum Active Power (WMax) <2> Percent of Maximum Reactive Power (VArMax) <3> Percent of Available Reactive Power (VArAvl) | 2 | 0 | 3 | 1 | 0 | Enum | DGEN.VArSetRef | 0 | AO5 | Operational Settings | M | M set to <2>
AI43 | System Available Active Generation Power | 2 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.MMXU.TotW | 0 |  | Monitoring | M
AI44 | System Available Active Charging Power | 2 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.MMXU.TotChaW | 0 |  | Monitoring | C: For Storage
AI45 | System Available Reactive Injection Power | 2 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarAvl | 0 |  | Monitoring | M
AI46 | System Available Reactive Absorption Power | 2 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarAvl | 0 |  | Monitoring | M
AI47 | System Available Actual State of Charge. Present energy in the DER as a percentage of Storage Effective Actual Capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DSTO.SocPct | 0 |  | Monitoring | C: For Storage
AI48 | System Usable State of Charge. Present usable energy in the DER as a percentage of Nameplate Storage Usable Capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DSTO.UseSocPct | 0 |  | Monitoring | C: For Storage | M
AI49 | System Start-up Status | 2 | -1 | 99 | 1 | 0 | Enum | DGEN.DEROpSt | 0 |  | Monitoring | M
AI50 | DER Start (Return to Service) Voltage High Limit. Percent of Reference Voltage. | 2 | 0 | 20000 | 0.01 | 0 | Percent | DCTE1.VHiLim | 0 | AO6 | Return to Service | M
AI51 | DER Start (Return to Service) Voltage Low Limit. Percent of Reference Voltage. | 2 | 0 | 10000 | 0.01 | 0 | Percent | DCTE1.VLoLim | 0 | AO7 | Return to Service | M
AI52 | DER Start (Return to Service) Frequency High Limit | 2 | 0 | 70000 | 0.001 | 0 | Hz | DCTE1.HzHiLim | 0 | AO8 | Return to Service | M
AI53 | DER Start (Return to Service) Frequency Low Limit | 2 | 0 | 70000 | 0.001 | 0 | Hz | DCTE1.HzLoLim | 0 | AO9 | Return to Service | M
AI54 | DER Start (Return to Service) Delay | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.RtnDlTmms | 0 | AO10 | Return to Service | M
AI55 | DER Start (Return to Service) Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.WinTms | 0 | AO11 | Return to Service
AI56 | DER Start (Return to Service) Ramp Up Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.RtnRmpTmms | 0 | AO12 | Return to Service
AI57 | DER Stop (Cease to Energize) Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.WinTms | 0 | AO13 | Cease
AI58 | DER Stop (Cease to Energize) Ramp Down Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.RmpTms | 0 | AO14 | Cease | M
AI59 | DER Stop (Cease to Energize) Reversion Timeout Period . Time to revert from the stopped state and return to service. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.RvrtTms | 0 | AO15 | Cease
AI60 | Connect/Disconnect Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE3.WinTms | 0 | AO16 | Connect
AI61 | Connect/Disconnect Reversion Timeout Period. Timeout (reversion time is for the Disconnect only) | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE3.RvrtTms | 0 | AO17 | Connect
AI62 | Maximum Generation Ramp Up Rate. The maximum generation ramp up rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DCTE.RpuRteMax | 0 |  | Operational Settings | M
AI63 | Maximum Generation Ramp Down Rate. The maximum generation ramp down rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DCTE.RpdRteMax | 0 |  | Operational Settings | M
AI64 | Maximum Charging Ramp Up Rate. The maximum charging ramp up rate expressed as a percentage of the Maximum Charging Rate (WChaMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DCTE.RpuChaRteMax | 0 |  | Operational Settings
AI65 | Maximum Charging Ramp Down Rate. The maximum charging ramp down rate expressed as a percentage of the Maximum Charnging Rate (WChaMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DCTE.RpdChaRteMax | 0 |  | Operational Settings
AI66 | Requested Islanded Condition. Enumeration: <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 2 | 0 | 255 | 1 | 0 | Enum | DECP1.EcpIsldSt | 0 |  | Operational Settings
AI67 | Islanded Condition Being Edited. Enumeration: <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 2 | 0 | 255 | 1 | 0 | Enum | DECPn.EcpIsldSt | 0 |  | Operational Settings
AI68 | Islanded Condition. Note this may differ from the Requested Island analog outputs depending on whether communications has been lost and how the Enable Sensed Grid Config Detection binary output is set. <0> Not Used <1> Unspecified / Autonomously Determined (see BO42) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 2 | 0 | 255 | 1 | 0 | Enum | DECP.EcpIsldSt | 0 |  | Operational Settings
AI69 | Freeze Counter Interval. interval between freeze counter operations after the initial occurrence. A zero value means the free counter operation is not repeated. | 2 | 0 | 2147483647 | 1 | 0 | n/a | MESA.FrzIntv | 0 |  | Metering
AI70 | Freeze Counter Interval Units. Units of the interval between freeze counter operations: <0> The outstation does not repeat the action, regardless of the Interval count. <1> Milliseconds - In tInverters case the interval is always counted relative to the Start Time and is constant regardless of the clock time set at the Outstation. <2> Seconds - At the same millisecond witInvertern the second that is specified in the Start Time. <3> Minutes - At the same second and millisecond witInvertern the minute that is specified in the Start Time. <4> Hours - At the same minute, second and B7millisecond witInvertern the hour that is specified in the Start Time. <5> Days - At the same time of day that is specified in the Start Time. <6> Weeks - On the same day of the week at the same time of day that is specified in the Start Time <7> Months - On the same day of each month at the same time of day that is specified in the Start Time. If the Start Time falls on the 29th or greater day of the month, the outstation shall not perform the action in months that do not have such a day <8> Months on Same Day of Week from Start of Month - At the same timeof day on the same day of the week after the beginning of the month as the day specified in the Start Time. For instance, if the Start Time specifies the second Tuesday of February and the Interval Count is 2, the next action shall occur on the second Tuesday of April. In the same example, if the Interval Count is set to 12, tInverters is the same as specifying, “Every year on the second Tuesday in February”. If the specified day does not occur in a given month when an action was scheduled to occur, the outstation shall not perform the action that month but shall perform it at the next valid scheduled time. <9> Months on Same Day of Week from End of Month - The outstation shall interpret tInverters setting as in <8>, but the day of the week shall be measured from the end of the month, e.g.,“the second-last Tuesday in February”. | 2 | 0 | 9 | 1 | 0 | Enum | MESA.FrzIntvUnt | 0 | AO21 | Metering
AI71 | Low/High Voltage Ride-Through Signal Meter ID. Referenced ECP. TInverters is the meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHVT.EcpRef | 0 | AO22 | Volt Ride-Through | C: For Function
AI72 | Low/High Voltage Ride-Through Voltage Reference Input. Active voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DHVT.MMXN.Vol | 0 |  | Volt Ride-Through | C: For Function
AI73 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV1.BlkRef | 0 | AO23 | Volt Ride-Through | C: For Function
AI74 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV1.BlkRef | 0 | AO24 | Volt Ride-Through | C: For Function
AI75 | Low/High Voltage Ride-Through High Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation / discharging must stop when the voltage is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV2.BlkRef | 0 | AO25 | Volt Ride-Through | C: For Function
AI76 | Low/High Voltage Ride-Through Low Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation / discharging must stop when the voltage is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV2.BlkRef | 0 | AO26 | Volt Ride-Through | C: For Function
AI77 | Low/High Frequency Ride-Through Signal Meter ID. Referenced ECP. TInverters is the meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFT.EcpRef | 0 | AO27 | Freq Ride-Through | C: For Function
AI78 | Low/High Frequency Ride-Through Frequency Reference Input. Active frequency measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DHFT.MMXU.Hz | 0 |  | Freq Ride-Through | C: For Function
AI79 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF1.BlkRef | 0 | AO28 | Freq Ride-Through | C: For Function
AI80 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF1.BlkRef | 0 | AO29 | Freq Ride-Through | C: For Function
AI81 | Low/High Frequency Ride-Through High Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation / discharging must stop when the frequency is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF2.BlkRef | 0 | AO30 | Freq Ride-Through | C: For Function
AI82 | Low/High Frequency Ride-Through Low Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation / discharging must stop when the frequency is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF2.BlkRef | 0 | AO31 | Freq Ride-Through | C: For Function
AI83 | Dynamic Reactive Current Support Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DRGS.ModPrio | 0 | AO32 | Dyn React Curr Supp | C: For Function
AI84 | Dynamic Reactive Current Support Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.WinTms | 0 | AO33 | Dyn React Curr Supp
AI85 | Dynamic Reactive Current Support Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.RmpTms | 0 | AO34 | Dyn React Curr Supp
AI86 | Dynamic Reactive Current Support Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.RvrtTms | 0 | AO35 | Dyn React Curr Supp
AI87 | Dynamic Reactive Current Support Signal Meter ID. Referenced ECP meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DRGS.EcpRef | 0 | AO36 | Dyn React Curr Supp | C: For Function
AI88 | Dynamic Reactive Current Support Voltage Reference Input. Votltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DRGS.MMXN.Vol | 0 |  | Dyn React Curr Supp | C: For Function
AI89 | Dynamic Reactive Current Support Moving Average Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DRGS.VAv | 0 |  | Dyn React Curr Supp | C: For Function
AI90 | Dynamic Reactive Current Support Present Delta Voltage. Difference in Volts between the present measured Voltage and the Moving Average Voltage as a percentage of the reference voltage | 2 | -10000 | 10000 | 0.1 | 0 | Percent | DRGS.DelV | 0 |  | Dyn React Curr Supp | C: For Function
AI91 | Dynamic Reactive Current Support - Gradient Mode. Enumeration: <0> Undefined <1> Gradients reach 0 at the moving average Voltage <2> Gradients reach 0 at the Voltage deadbands | 2 | 0 | 2 | 1 | 0 | Enum | DRGS.ArGraMod | 0 | AO37 | Dyn React Curr Supp | C: For Function
AI92 | Dynamic Reactive Current Support Deadband Minimum Voltage. Percentage of the nominal voltage, measured from the moving average voltage. Support is no longer applied when the voltage stays above tInverters value for the length of the Hold Time. | 2 | -10000 | 0 | 0.1 | 0 | Percent | DRGS.DbVMin | 0 | AO38 | Dyn React Curr Supp | C: For Function
AI93 | Dynamic Reactive Current Support Deadband Maximum Voltage. Percentage of the nominal voltage, measured from the moving average voltage. Support is no longer applied when the voltage stays below tInverters value for the length of the Hold Time. | 2 | 0 | 10000 | 0.1 | 0 | Percent | DRGS.DbVMax | 0 | AO39 | Dyn React Curr Supp | C: For Function
AI94 | Dynamic Reactive Current Support Gradient for Sags. Percentage of the rated current to apply capacitively per percentage of the negative deviation from the moving average voltage. It is a ratio of percent and is therefore unitless. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSag | 0 | AO40 | Dyn React Curr Supp | C: For Function
AI95 | Dynamic Reactive Current Support Gradient for Swells. Percentage of the rated current to apply inductively per percentage of the positive deviation from the moving average voltage. It is a ratio of percent and is therefore unitless. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSwl | 0 | AO41 | Dyn React Curr Supp | C: For Function
AI96 | Dynamic Reactive Current Support Filter Time for Moving Average Voltage. Used to determine amount of dynamic reactive current support. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.FilTms | 0 | AO42 | Dyn React Curr Supp | C: For Function
AI97 | Dynamic Reactive Current Support Block Zone Voltage. Percentage of the nominal voltage below which no reactive current support shall be applied. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DRGS.BlkZnV | 0 | AO43 | Dyn React Curr Supp | C: For Function
AI98 | Dynamic Reactive Current Support Hysteresis Block Zone Voltage. Percentage of the nominal voltage. After being blocked, reactive current support shall not resume until the voltage has been above the hysteresis block zone. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DRGS.HysBlkZnV | 0 | AO44 | Dyn React Curr Supp | C: For Function
AI99 | Dynamic Reactive Current Support Block Zone Time. Time in milliseconds from the beginning of any "sag" event, before which dynamic reactive current support will always continue, regardless of how low voltage may sag. | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.BlkZnTmms | 0 | AO45 | Dyn React Curr Supp | C: For Function
AI100 | Dynamic Reactive Current Support Hold Time. When the voltage returns to witInvertern the deadband limits for tInverters length of time (measured in milliseconds), the "sag" or "swell" event is considered to be over. Reactive current support ends, frozen values are unfrozen, and a new event can begin. | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.HoldTmms | 0 | AO47 | Dyn React Curr Supp | C: For Function
AI101 | Dynamic Reactive Current Attempted Output. Current output that the mode is attempting to achieve based on the Voltage input and other parameters. | 2 | 0 | 2147483647 | 0.1 | 0 | Amps | DRGS.ReqA | 0 |  | Dyn React Curr Supp | C: For Function
AI102 | Dynamic Volt-Watt Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVWD.ModPrio | 0 | AO48 | Dyn Volt-Watt | C: For Function
AI103 | Dynamic Volt-Watt Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.WinTms | 0 | AO49 | Dyn Volt-Watt
AI104 | Dynamic Volt-Watt Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.RmpTms | 0 | AO50 | Dyn Volt-Watt
AI105 | Dynamic Volt-Watt Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.RvrtTms | 0 | AO51 | Dyn Volt-Watt
AI106 | Dynamic Volt-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWD.EcpRef | 0 | AO52 | Dyn Volt-Watt | C: For Function
AI107 | Dynamic Volt-Watt Voltage Reference Input. Votltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWD.MMXN.Vol | 0 |  | Dyn Volt-Watt | C: For Function
AI108 | Dynamic Volt-Watt Moving Average Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWD.VAv | 0 |  | Dyn Volt-Watt | C: For Function
AI109 | Dynamic Volt-Watt Present Delta Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWD.DelV | 0 |  | Dyn Volt-Watt | C: For Function
AI110 | Dynamic Volt-Watt Gradient. Signed quantity that establishes the ratio of additional Watts supplied to the present difference from the moving average voltage. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent voltage difference | DVWD.DynVWGra | 0 | AO53 | Dyn Volt-Watt | C: For Function
AI111 | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.VWFilTms | 0 | AO54 | Dyn Volt-Watt | C: For Function
AI112 | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage measured below the moving average voltage. If the present voltage is above tInverters value, no additional Watts shall be supplied. | 2 | -1000 | 0 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWLo | 0 | AO55 | Dyn Volt-Watt | C: For Function
AI113 | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage measured above the moving average voltage. If the present voltage is below tInverters value, no additional Watts shall be supplied. | 2 | 0 | 1000 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWInverter | 0 | AO56 | Dyn Volt-Watt | C: For Function
AI114 | Dynamic Volt-Watt Attempted Output. Watt output that the mode is attempting to achieve based on the Voltage input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DVWD.ReqWSet | 0 |  | Dyn Volt-Watt | C: For Function
AI115 | Frequency-Watt Mode Priority |  | 0 | 100 | 1 | 0 | n/a | DHFW1.ModPrio | 0 | AO57 | Freq-Watt | C: For Function
AI116 | Frequency-Watt Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.WinTms | 0 | AO58 | Freq-Watt
AI117 | Frequency-Watt Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.RmpTms | 0 | AO59 | Freq-Watt
AI118 | Frequency-Watt Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.RvrtTms | 0 | AO60 | Freq-Watt
AI119 | Frequency-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW1.EcpRef | 0 | AO61 | Freq-Watt | C: For Function
AI120 | Frequency-Watt Frequency Reference Input. Frequency measurement read from the meter and used as an input to the mode. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.MMXU.Hz | 0 |  | Freq-Watt | C: For Function
AI121 | Frequency-Watt High Starting Frequency. Delta frequency between start frequency and nominal grid frequency for High frequency events. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | 0 | AO62 | Freq-Watt | C: For Function | M
AI122 | Frequency-Watt High Stopping Frequency. Delta frequency between stop frequency and nominal grid frequency for High frequency events. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStop | 0 | AO63 | Freq-Watt
AI123 | Frequency-Watt High Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | 0 | AO64 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI586 | M
AI124 | Frequency-Watt High Charging Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent frequency difference | DHFW1.WChaGra | 0 | AO65 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI586
AI125 | Frequency-Watt Low Starting Frequency. Delta frequency between start frequency and nominal grid frequency for low frequency events. | 2 | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | 0 | AO66 | Freq-Watt | C: For Function | M
AI126 | Frequency-Watt Low Stopping Frequency. Delta frequency between stop frequency and nominal grid frequency for low frequency events. | 2 | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStop | 0 | AO67 | Freq-Watt
AI127 | Frequency-Watt Low Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | 0 | AO68 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI587 | M
AI128 | Frequency-Watt Low Charging Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent frequency difference | DLFW1.WChaGra | 0 | AO69 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI587
AI129 | Frequency-Watt Start Delay | 2 | 0 | 2147483647 | 1 | 0 | ms | DHFW1.ActStrDlTmms | 0 | AO70 | Freq-Watt
AI130 | Frequency-Watt Stop Delay | 2 | 0 | 2147483647 | 1 | 0 | ms | DHFW1.ActStopDlTmms | 0 | AO71 | Freq-Watt
AI131 | Frequency-Watt Ramp Up Time Constant. Time constant or open loop response time for moving from the current active power target to a Higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DLFW1.OplTmsMax.1 | 0 | AO72 | Freq-Watt | C: For Function | M
AI132 | Frequency-Watt Ramp Down Time Constant. Time constant or open loop response time for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | 0 | AO73 | Freq-Watt |  | M
AI133 | Frequency-Watt Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.RpuRte | 0 | AO74 | Freq-Watt
AI134 | Frequency-Watt Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.RpdRteMax | 0 | AO75 | Freq-Watt
AI135 | Frequency-Watt Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.RpuChaRte | 0 | AO76 | Freq-Watt
AI136 | Frequency-Watt Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW1.RpdChaRteMax | 0 | AO77 | Freq-Watt
AI137 | Frequency-Watt High Return Gradient | 2 | 0 | 1000 | 0.1 | 0 | Percent watts per percent Hz difference | DHFW1.RtnRmpRte | 0 | AO78 | Freq-Watt
AI138 | Frequency-Watt Low Return Gradient | 2 | 0 | 1000 | 0.1 | 0 | Percent watts per percent Hz difference | DLFW1.RtnRmpRte | 0 | AO79 | Freq-Watt
AI139 | Frequency-Watt Attempted Output. Watt output that the mode is attempting to achieve based on the frequency input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DHFW1.ReqWLim | 0 |  | Freq-Watt
AI140 | Frequency-Watt Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DHFW1.SocUseMinPct | 0 | AO80 | Freq-Watt
AI141 | Frequency-Watt Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DHFW1.SocUseMaxPct | 0 | AO81 | Freq-Watt
AI142 | Active Power Limit Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWMX.ModPrio | 0 | AO82 | Active Power Limit | C: For Function
AI143 | Active Power Limit Enabling Time Window. Time window (in seconds) witInvertern which to randomly execute a command. If the time window is zero, the command will be executed immediately | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWMX.WinTms | 0 | AO83 | Active Power Limit
AI144 | Active Power Limit Enabling Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWMX.RmpTms | 0 | AO84 | Active Power Limit
AI145 | Active Power Limit Reversion Timeout Period. Reversion Timeout Period (in seconds), after which the device will revert to its default status, such as closing the switch to reconnect to the grid or allowing maximum watts output, in case communications are lost or mitigating messages are not received | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWMX.RvrtTms | 0 | AO85 | Active Power Limit
AI146 | Active Power Limit Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWMX.EcpRef | 0 | AO86 | Active Power Limit | C: For Function
AI147 | Active Power Limit Reference Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.MMXU.TotW | 0 |  | Active Power Limit | C: For Function
AI148 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | 0 | AO87 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI588 | M
AI149 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | 0 | AO88 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI589 | M
AI150 | Charge/Discharge Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWGC.ModPrio | 0 | AO89 | Set Active Power | C: For Function
AI151 | Charge/Discharge Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.WinTms | 0 | AO90 | Set Active Power
AI152 | Charge/Discharge Enabling Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.RmpTms | 0 | AO91 | Set Active Power
AI153 | Charge/Discharge Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.RvrtTms | 0 | AO92 | Set Active Power
AI154 | Charge/Discharge Active Power Target. Percentage of maximum active power. | 2 | -1000 | 1000 | 0.1 | 0 | Percent of WMax | DWGC.GnWPctSpt | 0 | AO93 | Set Active Power | C: For Function if BO46 = 0
AI155 | Charge/Discharge Ramp Up Time Constant. Ramp time, in seconds, for moving from the current active power target to a higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.1 | 0 | AO94 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI156 | Charge/Discharge Ramp Down Time Constant. Ramp time, in seconds, for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.2 | 0 | AO95 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI157 | Charge/Discharge Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpuRte | 0 | AO96 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI158 | Charge/Discharge Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpdRteMax | 0 | AO97 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI159 | Charge/Discharge Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpuChaRte | 0 | AO98 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI160 | Charge/Discharge Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpdChaRteMax | 0 | AO99 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI161 | Charge/Discharge Minimum Reserve for Storage. The reserve level below which the storage system may only be discharged in emergency situations, expressed as a percentage of the usable capacity. | 2 | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMinPct | 0 | AO100 | Set Active Power | C: For Storage
AI162 | Charge/Discharge Maximum Reserve for Storage. The reserve level above which the storage system may only be charged in emergency situations, expressed as a percentage of the usable capacity. | 2 | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMaxPct | 0 | AO101 | Set Active Power | C: For Storage
AI163 | Coordinated Charge/Discharge Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DTCD.ModPrio | 0 | AO102 | Coord Charge-Dischg | C: For Storage
AI164 | Coordinated Charge/Discharge Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.WinTms | 0 | AO103 | Coord Charge-Dischg
AI165 | Coordinated Charge/Discharge Enabling Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.RmpTms | 0 | AO104 | Coord Charge-Dischg
AI166 | Coordinated Charge/Discharge Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.RvrtTms | 0 | AO105 | Coord Charge-Dischg
AI167 | Coordinated Charge/Discharge Target State of Charge. Charge that the system is expected to achieve, as a percentage of the usable capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DTCD.SocUseTgtPct | 0 | AO106 | Coord Charge-Dischg | C: For Storage
AI168 | Coordinated Charge/Discharge Target Date. Date by which the storage system must reach the target SOC. Days since January 1, 1970, UTC. | 2 | 0 | 2147483647 | 1 | 0 | Days | DTCD.DateTgt.Date | 0 | AO107 | Coord Charge-Dischg | C: For Storage
AI169 | Coordinated Charge/Discharge Target Time. Time by when the storage system must reach the target SOC. Expressed as the number of seconds since the start of Target Date. | 2 | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.DateTgt.Time | 0 | AO108 | Coord Charge-Dischg | C: For Storage
AI170 | Coordinated Charge/Discharge Energy Request. Amount of energy that must be transferred from the grid to the charger to move the SOC from the value at the specific time of reference to the target SOC. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hours | DTCD.WhReq | 0 | AO109 | Coord Charge-Dischg | C: For Storage
AI171 | Coordinated Charge/Discharge Minimum Charging Duration. Minimum duration to move from the SOC at the time of reference to the target SOC. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurTms | 0 | AO110 | Coord Charge-Dischg | C: For Storage
AI172 | Coordinated Charge/Discharge Date of Reference. Date that the SOC is measured or computed by the storage system and is the basis for the Energy Request, Minimum Charging Duration, and other parameters | 2 | 0 | 2147483647 | 1 | 0 | Days | DTCD.SocDate | 0 | AO111 | Coord Charge-Dischg | C: For Storage
AI173 | Coordinated Charge/Discharge Time of Reference. Time that the SOC is measured or computed by the storage system and is the basis for the Energy Request, Minimum Charging Duration, and other parameters | 2 | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.SocDateTms | 0 | AO112 | Coord Charge-Dischg | C: For Storage
AI174 | Coordinated Charge/Discharge Duration at Maximum Charge Rate. Duration that energy can be stored at the Maximum Charge Rate. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurMax | 0 | AO113 | Coord Charge-Dischg | C: For Storage
AI175 | Coordinated Charge/Discharge Duration Maximum Discharge Rate. Duration that energy can be delivered at the Maximum Discharge Rate. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.DschDurMax | 0 | AO114 | Coord Charge-Dischg | C: For Storage
AI176 | Active Power Following Mode #1 (Peak Power Limiting) Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWFL1.ModPrio | 0 | AO115 | Peak Power Limiting | C: For Function
AI177 | Active Power Following Mode #1 (Peak Power Limiting) Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL1.WinTms | 0 | AO116 | Peak Power Limiting
AI178 | Active Power Following Mode #1 (Peak Power Limiting) Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL1.RmpTms | 0 | AO117 | Peak Power Limiting
AI179 | Active Power Following Mode #1 (Peak Power Limiting) Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL1.RvrtTms | 0 | AO118 | Peak Power Limiting
AI180 | Active Power Following Mode #1 (Peak Power Limiting) Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWFL1.EcpRef | 0 | AO119 | Peak Power Limiting | C: For Function
AI181 | Active Power Following Mode #1 (Peak Power Limiting) Reference Power Measured | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.MMXU.TotW | 0 |  | Peak Power Limiting | C: For Function
AI182 | Active Power Following Mode #1 (Peak Power Limiting) Power Threshold | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.FolWThr | 0 | AO120 | Peak Power Limiting | C: For Function
AI183 | Active Power Following Mode #1 (Peak Power Limiting) Ratio. Percent of the power exceeding the Power Threshold | 2 | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL1.FolWPct | 0 | AO121 | Peak Power Limiting | C: For Function
AI184 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpuRte | 0 | AO122 | Peak Power Limiting | C: For Function
AI185 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpdRte | 0 | AO123 | Peak Power Limiting | C: For Function
AI186 | Active Power Following Mode #1 (Peak Power Limiting) Attempted Output. Watt output that the mode is attempting to achieve based on the Watts input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.ReqW | 0 |  | Peak Power Limiting | C: For Function
AI187 | Active Power Following Mode #2 (Load Following) Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWFL2.ModPrio | 0 | AO124 | Load Following | C: For Function
AI188 | Active Power Following Mode #2 (Load Following) Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL2.WinTms | 0 | AO125 | Load Following
AI189 | Active Power Following Mode #2 (Load Following) Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL2.RmpTms | 0 | AO126 | Load Following
AI190 | Active Power Following Mode #2 (Load Following) Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL2.RvrtTms | 0 | AO127 | Load Following
AI191 | Active Power Following Mode #2 (Load Following) Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWFL2.EcpRef | 0 | AO128 | Load Following | C: For Function
AI192 | Active Power Following Mode #2 (Load Following) Reference Power Measured | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.MMXU.TotW | 0 |  | Load Following | C: For Function
AI193 | Active Power Following Mode #2 (Load Following) Power Threshold | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.FolWThr | 0 | AO129 | Load Following | C: For Function
AI194 | Active Power Following Mode #2 (Load Following) Ratio. Percent of the power exceeding the Power Threshold | 2 | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL2.FolWPct | 0 | AO130 | Load Following | C: For Function
AI195 | Active Power Following Mode #2 (Load Following) Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpuRte | 0 | AO131 | Load Following | C: For Function
AI196 | Active Power Following Mode #2 (Load Following) Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpdRte | 0 | AO132 | Load Following | C: For Function
AI197 | Active Power Following Mode #2 (Load Following) Attempted Output. Watt output that the mode is attempting to achieve based on the Watts input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.ReqW | 0 |  | Load Following | C: For Function
AI198 | Active Power Following Mode #3 (Generation Following) Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWFL3.ModPrio | 0 | AO133 | Generation Following | C: For Function
AI199 | Active Power Following Mode #3 (Generation Following) Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL3.WinTms | 0 | AO134 | Generation Following
AI200 | Active Power Following Mode #3 (Generation Following) Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL3.RmpTms | 0 | AO135 | Generation Following
AI201 | Active Power Following Mode #3 (Generation Following) Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWFL3.RvrtTms | 0 | AO136 | Generation Following
AI202 | Active Power Following Mode #3 (Generation Following) Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWFL3.EcpRef | 0 | AO137 | Generation Following | C: For Function
AI203 | Active Power Following Mode #3 (Generation Following) Reference Power Measured | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.MMXU.TotW | 0 |  | Generation Following | C: For Function
AI204 | Active Power Following Mode #3 (Generation Following) Power Threshold | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.FolWThr | 0 | AO138 | Generation Following | C: For Function
AI205 | Active Power Following Mode #3 (Generation Following) Ratio. Percent of the power exceeding the Power Threshold | 2 | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL3.FolWPct | 0 | AO139 | Generation Following | C: For Function
AI206 | Active Power Following Mode #3 (Generation Following) Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpuRte | 0 | AO140 | Generation Following | C: For Function
AI207 | Active Power Following Mode #3 (Generation Following) Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpdRte | 0 | AO141 | Generation Following | C: For Function
AI208 | Active Power Following Mode #3 (Generation Following) Attempted Output. Watt output that the mode is attempting to achieve based on the Watts input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.ReqW | 0 |  | Generation Following | C: For Function
AI209 | AGC Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DAGC.ModPrio | 0 | AO142 | AGC | C: For Function
AI210 | AGC Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.WinTms | 0 | AO143 | AGC
AI211 | AGC Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RmpTms | 0 | AO144 | AGC
AI212 | AGC Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RvrtTms | 0 | AO145 | AGC
AI213 | AGC Active Power Target | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WSpt | 0 | AO146 | AGC | C: For Function
AI214 | AGC Ramp Up Time Constant. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RmpUpTms | 0 | AO147 | AGC | C: For Function
AI215 | AGC Ramp Down Time Constant. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RmpDnTms | 0 | AO148 | AGC | C: For Function
AI216 | AGC Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpuRte | 0 | AO149 | AGC | C: For Function
AI217 | AGC Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpdRte | 0 | AO150 | AGC | C: For Function
AI218 | AGC Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpuChaRte | 0 | AO151 | AGC | C: For Storage
AI219 | AGC Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpdChaRte | 0 | AO152 | AGC | C: For Storage
AI220 | AGC Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMinPct | 0 | AO153 | AGC | C: For Storage
AI221 | AGC Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMaxPct | 0 | AO154 | AGC | C: For Storage
AI222 | AGC Maximum Watts Available | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WMaxAvl | 0 |  | AGC | C: For Function
AI223 | AGC Minimum Watts Available | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WMinAvl | 0 |  | AGC | C: For Function
AI224 | AGC Expected State of Charge | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocExpc | 0 |  | AGC | C: For Function
AI225 | AGC Expected State of Energy | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocWhExpc | 0 |  | AGC | C: For Function
AI226 | AGC Expected State of Charge Time Interval | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.SocExpcTms | 0 |  | AGC | C: For Function
AI227 | Active Power Smoothing Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWSM.ModPrio | 0 | AO155 | Active Power Smoothing | C: For Function
AI228 | Active Power Smoothing Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.WinTms | 0 | AO156 | Active Power Smoothing
AI229 | Active Power Smoothing Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.RmpTms | 0 | AO157 | Active Power Smoothing
AI230 | Active Power Smoothing Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.RvrtTms | 0 | AO158 | Active Power Smoothing
AI231 | Active Power Smoothing Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWSM.EcpRef | 0 | AO159 | Active Power Smoothing | C: For Function
AI232 | Active Power Smoothing Reference Power Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWSM.MMXU.TotW | 0 |  | Active Power Smoothing | C: For Function
AI233 | Active Power Smoothing Gradient. Signed quantity that establishes the ratio of additional smoothing Watts provided to the present delta-watts of the reference load or generation. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Watts per delta-watt | DWSM.WSmthGra | 0 | AO160 | Active Power Smoothing | C: For Function
AI234 | Active Power Smoothing Lower Limit. Difference in Watts from the moving average of the reference power above which no smoothing shall be applied. | 2 | -2147483648 | 0 | 1 | 0 | Watts | DWSM.WSmthLoLim | 0 | AO161 | Active Power Smoothing | C: For Function
AI235 | Active Power Smoothing Upper Limit. Difference in Watts from the moving average of the reference power below which no smoothing shall be applied. | 2 | 0 | 2147483647 | 1 | 0 | Watts | DWSM.WSmthhiLim | 0 | AO162 | Active Power Smoothing | C: For Function
AI236 | Active Power Smoothing Filter Time (Seconds). Time in seconds used to calculate the moving average of the reference load or generation being smoothed. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.FilTms | 0 | AO163 | Active Power Smoothing | C: For Function
AI237 | Active Power Smoothing Discharge Ramp Up Rate. The maximum generation ramp up rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpuRte | 0 | AO164 | Active Power Smoothing | C: For Function
AI238 | Active Power Smoothing Discharge Ramp Down Rate. The maximum generation ramp down rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpdRte | 0 | AO165 | Active Power Smoothing | C: For Function
AI239 | Active Power Smoothing Charge Ramp Up Rate. The maximum charging ramp up rate expressed as a percentage of the Maximum Charging Rate (WChaMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpuChaRte | 0 | AO166 | Active Power Smoothing | C: For Storage
AI240 | Active Power Smoothing Charge Ramp Down Rate. The maximum charging ramp down rate expressed as a percentage of the Maximum Charnging Rate (WChaMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpdChaRte | 0 | AO167 | Active Power Smoothing | C: For Storage
AI241 | Active Power Smoothing Attempted Output. Watt output that the mode is attempting to achieve based on the Watt input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWSM.ReqWSet | 0 |  | Active Power Smoothing | C: For Function
AI242 | Volt-Watt Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVWC1.ModPrio | 0 | AO168 | Volt-Watt | C: For Function
AI243 | Volt-Watt Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.WinTms | 0 | AO169 | Volt-Watt
AI244 | Volt-Watt Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.RmpTms | 0 | AO170 | Volt-Watt
AI245 | Volt-Watt Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.RvrtTms | 0 | AO171 | Volt-Watt
AI246 | Volt-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | 0 | AO172 | Volt-Watt | C: For Function | M
AI247 | Volt-Watt Reference Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.MMXN.Vol | 0 |  | Volt-Watt | C: For Function | M
AI248 | Volt-Watt Curve Index. Index of the Volt-Watt curve that should be used by the mode. If zero, then direct paramters are used. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | 0 | AO173 | Volt-Watt | C: For Function | M
AI249 | Volt-Watt Attempted Output. Maximum active power the outstation is permitted to generate or absorb based on the voltage level and gradient. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DVWC1.ReqWLim | 0 |  | Volt-Watt | C: For Function
AI250 | Volt-Watt Filter Time (Seconds) | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.FilTms | 0 | AO174 | Volt-Watt | C: For Function
AI251 | Volt-Watt Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.1 | 0 | AO175 | Volt-Watt | C: For Function
AI252 | Volt-Watt Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.2 | 0 | AO176 | Volt-Watt | C: For Function
AI253 | Volt-Watt Discharging Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuRte | 0 | AO177 | Volt-Watt | C: For Function
AI254 | Volt-Watt Discharging Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdRte | 0 | AO178 | Volt-Watt | C: For Function
AI255 | Volt-Watt Charging Ramp Up Rate. Maximum charging ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuChaRte | 0 | AO179 | Volt-Watt | C: For Function
AI256 | Volt-Watt Charging Ramp Down Rate. Maximum charging ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdChaRte | 0 | AO180 | Volt-Watt | C: For Function
AI257 | Frequency-Watt Curve Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DHFW2.ModPrio | 0 | AO181 | Freq-Watt Curve | C: For Function
AI258 | Frequency-Watt Curve Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.WinTms | 0 | AO182 | Freq-Watt Curve
AI259 | Frequency-Watt Curve Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.RmpTms | 0 | AO183 | Freq-Watt Curve
AI260 | Frequency-Watt Curve Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.RvrtTms | 0 | AO184 | Freq-Watt Curve
AI261 | Frequency-Watt Curve Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.EcpRef | 0 | AO185 | Freq-Watt Curve | C: For Function
AI262 | Frequency-Watt Curve Frequency Reference Input. Frequency measurement read from the meter and used as an input to the mode. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW2.MMXU.Hz | 0 |  | Freq-Watt Curve | C: For Function
AI263 | Frequency-Watt Curve - Curve Index. Index of the Frequency-Watt curve that should be used by the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HzWCrv | 0 | AO186 | Freq-Watt Curve | C: For Function
AI264 | Frequency-Watt Curve - High Frequency Hysteresis Curve Index. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HysCrv | 0 | AO187 | Freq-Watt Curve | C: For Function
AI265 | Frequency-Watt Curve - Low Frequency Hysteresis Curve Index. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLFW2.HysCrv | 0 | AO188 | Freq-Watt Curve | C: For Function
AI266 | Frequency-Watt Curve Start Delay | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStrDlTmms | 0 | AO189 | Freq-Watt Curve | C: For Function
AI267 | Frequency-Watt Curve Stop Delay | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStopDlTmms | 0 | AO190 | Freq-Watt Curve | C: For Function
AI268 | Frequency-Watt Curve Ramp Up Time Constant. Time constant or open loop response time for moving from the current active power target to a higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.1 | 0 | AO191 | Freq-Watt Curve | C: For Function
AI269 | Frequency-Watt Curve Ramp Down Time Constant. Time constant or open loop response time for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.2 | 0 | AO192 | Freq-Watt Curve | C: For Function
AI270 | Frequency-Watt Curve Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuRte | 0 | AO193 | Freq-Watt Curve | C: For Function
AI271 | Frequency-Watt Curve Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdRte | 0 | AO194 | Freq-Watt Curve | C: For Function
AI272 | Frequency-Watt Curve Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuChaRte | 0 | AO195 | Freq-Watt Curve | C: For Storage
AI273 | Frequency-Watt Curve Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdChaRte | 0 | AO196 | Freq-Watt Curve | C: For Storage
AI274 | Frequency-Watt Attempted Output. Watt output that the mode is attempting to achieve based on the Frequency input and selected curve. If “Snapshot of Power” is not enabled, this is the maximum active power the outstation will attempt to generate or absorb. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DHFW2.ReqWLim | 0 |  | Freq-Watt Curve | C: For Function
AI275 | Frequency-Watt Curve Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMinPct | 0 | AO197 | Freq-Watt Curve | C: For Storage
AI276 | Frequency-Watt Curve Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMaxPct | 0 | AO198 | Freq-Watt Curve | C: For Storage
AI277 | Constant VArs Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVAR.ModPrio | 0 | AO199 | Const VArs | C: For Function
AI278 | Constant VArs Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.WinTms | 0 | AO200 | Const VArs
AI279 | Constant VArs Enabling Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.RmpTms | 0 | AO201 | Const VArs
AI280 | Constant VArs Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.RvrtTms | 0 | AO202 | Const VArs
AI281 | Constant VArs Reactive Power Target. Percentage of maximum reactive power. | 2 | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | 0 | AO203 | Const VArs | C: For Function | M
AI282 | Constant VArs Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.1 | 0 | AO204 | Const VArs | C: For Function
AI283 | Constant VArs Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.2 | 0 | AO205 | Const VArs | C: For Function
AI284 | Constant Power Factor Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DFPF.ModPrio | 0 | AO206 | Constant PF | C: For Function
AI285 | Constant Power Factor Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DFPF.WinTms | 0 | AO207 | Constant PF
AI286 | Constant Power Factor Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DFPF.RmpTms | 0 | AO208 | Constant PF
AI287 | Constant Power Factor Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DFPF.RvrtTms | 0 | AO209 | Constant PF
AI288 | Constant Power Factor Setpoint - Generation / Discharging | 2 | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | 0 | AO210 | Constant PF | C: For Function | M
AI289 | Constant Power Factor Setpoint - Charging | 2 | 0 | 100 | 0.01 | 0 | None | DFPF.PFLodTgt | 0 | AO211 | Constant PF | C: For Function
AI290 | Volt-Var Control Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVVR.ModPrio | 0 | AO212 | Volt-VAr | C: For Function
AI291 | Volt-VAr Control Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.WinTms | 0 | AO213 | Volt-VAr
AI292 | Volt-VAr Control Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.RmpTms | 0 | AO214 | Volt-VAr
AI293 | Volt-VAr Control Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.RvrtTms | 0 | AO215 | Volt-VAr
AI294 | Volt-VAr Control Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVVR.EcpRef | 0 | AO216 | Volt-VAr | C: For Function
AI295 | Volt-VAr Control Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVVR.MMXN.Vol | 0 |  | Volt-VAr | C: For Function
AI296 | Volt-VAr Control Adjusted Voltage Reference. The Voltage used as reference for Volt-VAr control. If Autonomous Voltage Reference Adjustment is disabled, this is the same fixed value as the Reference Voltage. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVVR.VRefSet | 0 |  | Volt-VAr | C: For Function
AI297 | Volt-VAr Curve Index. Index of the Volt-VAr curve that should be used by the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVVR.VVArCrv | 0 | AO217 | Volt-VAr | C: For Function
AI298 | Volt-VAr Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.1 | 0 | AO218 | Volt-VAr | C: For Function
AI299 | Volt-VAr Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.2 | 0 | AO219 | Volt-VAr | C: For Function
AI300 | Volt-VAr Autonomous Voltage Reference Adjustment Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.VRefTmms | 0 | AO220 | Volt-VAr | C: For Function
AI301 | Volt-VAr Attempted Output. VAr output that the mode is attempting to achieve based on the Voltage input and selected curve. | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DVVR.ReqVAr | 0 |  | Volt-VAr | C: For Function
AI302 | Watt-VAr Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWVR.ModPrio | 0 | AO221 | Watt-VAr | C: For Function
AI303 | Watt-VAr Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.WinTms | 0 | AO222 | Watt-VAr
AI304 | Watt-VAr Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.RmpTms | 0 | AO223 | Watt-VAr
AI305 | Watt-VAr Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.RvrtTms | 0 | AO224 | Watt-VAr
AI306 | Watt-VAr Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWVR.EcpRef | 0 | AO225 | Watt-VAr | C: For Function
AI307 | Watt-VAr Reference Power Input. Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | Watts | DWVR.MMXU.TotW | 0 |  | Watt-VAr | C: For Function
AI308 | Watt-VAr Curve Index. Index of the Watt-VAr curve that should be used by the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWVR.WVArCrv | 0 | AO226 | Watt-VAr | C: For Function
AI309 | Watt-VAr Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.1 | 0 | AO227 | Watt-VAr | C: For Function
AI310 | Watt-VAr Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.2 | 0 | AO228 | Watt-VAr | C: For Function
AI311 | Watt-VAr Attempted Output. VAr output that the mode is attempting to achieve based on the Watt input and selected curve. | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DWVR.ReqVAr | 0 |  | Watt-VAr | C: For Function
AI312 | Power Factor Correction Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DPFC.ModPrio | 0 | AO229 | PF Correct | C: For Function
AI313 | Power Factor Correction Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPFC.WinTms | 0 | AO230 | PF Correct
AI314 | Power Factor Correction Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPFC.RmpTms | 0 | AO231 | PF Correct
AI315 | Power Factor Correction Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPFC.RvrtTms | 0 | AO232 | PF Correct
AI316 | Power Factor Correction Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DPFC.EcpRef | 0 | AO233 | PF Correct | C: For Function
AI317 | Power Factor Correction Reference Power Factor Input. Power factor measurement read from the meter and used as an input to the mode. | 2 | -100 | 100 | 0.01 | 0 | None | DFPC.MMXU.TotPF | 0 |  | PF Correct | C: For Function
AI318 | Power Factor Correction Average PF Target | 2 | -100 | 100 | 0.01 | 0 | None | DPFC.PFTrg | 0 | AO234 | PF Correct | C: For Function
AI319 | Power Factor Correction Lower PF Limit | 2 | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.min | 0 | AO235 | PF Correct | C: For Function
AI320 | Power Factor Correction Upper PF Limit | 2 | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.max | 0 | AO236 | PF Correct | C: For Function
AI321 | Pricing Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DPRG.ModPrio | 0 | AO237 | Price | C: For Function
AI322 | Pricing Mode Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.WinTms | 0 | AO238 | Price
AI323 | Pricing Mode Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.RmpTms | 0 | AO239 | Price
AI324 | Pricing Mode Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.RvrtTms | 0 | AO240 | Price
AI325 | Pricing Mode Setpoint: Hundredths of local currency per Kilowatt-Hr. | 2 | -2147483648 | 2147483647 | 0.01 | 0 | 100ths of local currency | DPRG.PrcRef | 0 | AO241 | Price | C: For Function
AI326 | Pricing Mode Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.OplTmsMax.1 | 0 | AO242 | Price | C: For Function
AI327 | Pricing Mode Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.OplTmsMax.2 | 0 | AO243 | Price | C: For Function
AI328 | Curve Edit Selector | 2 | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | 1 | AO244 | Curve | M | C: See clause 1.7
AI329 | Curve Type. Enumeration: <0> Curve disabled <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-VAr <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 2 | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | 0 | AO245 | Curve | M | C: See clause 1.7
AI330 | Curve Number of Points | 2 | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | 0 | AO246 | Curve | M | C: See clause 1.7
AI331 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time <29> Voltage <33> Frequency <38> Watts <23> Celsius Temperature <100> Price in hundredths of local currency <129> Voltage as a percent of nominal voltage (VRef) <133> Frequency as a percent of nominal frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | 0 | AO247 | Curve | M | C: See clause 1.7
AI332 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> VArs as percent of max VArs (VARMax) <3> VArs as percent of max available VArs (VArAval) <4> Vars as percent of max apparent Watts (VAMax) - used in IEEE 1547 <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor in EEI notation <8> Volts as a percent of nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage <33> Frequency <38> Watts <99+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | 0 | AO248 | Curve | M | C: See clause 1.7
AI333 | Curve Point 1 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | 0 | AO249 | Curve | M | C: See clause 1.7
AI334 | Curve Point 1 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | 0 | AO250 | Curve | M | C: See clause 1.7
AI335 | Curve Point 2 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | 0 | AO251 | Curve | M | C: See clause 1.7
AI336 | Curve Point 2 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | 0 | AO252 | Curve | M | C: See clause 1.7
AI337 | Curve Point 3 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | 0 | AO253 | Curve | M | C: See clause 1.7
AI338 | Curve Point 3 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | 0 | AO254 | Curve | M | C: See clause 1.7
AI339 | Curve Point 4 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | 0 | AO255 | Curve | M | C: See clause 1.7
AI340 | Curve Point 4 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | 0 | AO256 | Curve | M | C: See clause 1.7
AI341 | Curve Point 5 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.xVal | 0 | AO257 | Curve | M
AI342 | Curve Point 5 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.yVal | 0 | AO258 | Curve | M
AI343 | Curve Point 6 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.xVal | 0 | AO259 | Curve | M
AI344 | Curve Point 6 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.yVal | 0 | AO260 | Curve | M
AI345 | Curve Point 7 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.xVal | 0 | AO261 | Curve | M
AI346 | Curve Point 7 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.yVal | 0 | AO262 | Curve | M
AI347 | Curve Point 8 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.xVal | 0 | AO263 | Curve | M
AI348 | Curve Point 8 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.yVal | 0 | AO264 | Curve | M
AI349 | Curve Point 9 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.xVal | 0 | AO265 | Curve | M
AI350 | Curve Point 9 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.yVal | 0 | AO266 | Curve | M
AI351 | Curve Point 10 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.xVal | 0 | AO267 | Curve | M
AI352 | Curve Point 10 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.yVal | 0 | AO268 | Curve | M
AI353 | Curve Point 11 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.11.xVal | 0 | AO269 | Curve
AI354 | Curve Point 11 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.11.yVal | 0 | AO270 | Curve
AI355 | Curve Point 12 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.12.xVal | 0 | AO271 | Curve
AI356 | Curve Point 12 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.12.yVal | 0 | AO272 | Curve
AI357 | Curve Point 13 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.13.xVal | 0 | AO273 | Curve
AI358 | Curve Point 13 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.13.yVal | 0 | AO274 | Curve
AI359 | Curve Point 14 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.14.xVal | 0 | AO275 | Curve
AI360 | Curve Point 14 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.14.yVal | 0 | AO276 | Curve
AI361 | Curve Point 15 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.15.xVal | 0 | AO277 | Curve
AI362 | Curve Point 15 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.15.yVal | 0 | AO278 | Curve
AI363 | Curve Point 16 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.16.xVal | 0 | AO279 | Curve
AI364 | Curve Point 16 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.16.yVal | 0 | AO280 | Curve
AI365 | Curve Point 17 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.17.xVal | 0 | AO281 | Curve
AI366 | Curve Point 17 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.17.yVal | 0 | AO282 | Curve
AI367 | Curve Point 18 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.18.xVal | 0 | AO283 | Curve
AI368 | Curve Point 18 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.18.yVal | 0 | AO284 | Curve
AI369 | Curve Point 19 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.19.xVal | 0 | AO285 | Curve
AI370 | Curve Point 19 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.19.yVal | 0 | AO286 | Curve
AI371 | Curve Point 20 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.20.xVal | 0 | AO287 | Curve
AI372 | Curve Point 20 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.20.yVal | 0 | AO288 | Curve
AI373 | Curve Point 21 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.21.xVal | 0 | AO289 | Curve
AI374 | Curve Point 21 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.21.yVal | 0 | AO290 | Curve
AI375 | Curve Point 22 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.22.xVal | 0 | AO291 | Curve
AI376 | Curve Point 22 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.22.yVal | 0 | AO292 | Curve
AI377 | Curve Point 23 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.23.xVal | 0 | AO293 | Curve
AI378 | Curve Point 23 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.23.yVal | 0 | AO294 | Curve
AI379 | Curve Point 24 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.24.xVal | 0 | AO295 | Curve
AI380 | Curve Point 24 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.24.yVal | 0 | AO296 | Curve
AI381 | Curve Point 25 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.25.xVal | 0 | AO297 | Curve
AI382 | Curve Point 25 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.25.yVal | 0 | AO298 | Curve
AI383 | Curve Point 26 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.26.xVal | 0 | AO299 | Curve
AI384 | Curve Point 26 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.26.yVal | 0 | AO300 | Curve
AI385 | Curve Point 27 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.27.xVal | 0 | AO301 | Curve
AI386 | Curve Point 27 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.27.yVal | 0 | AO302 | Curve
AI387 | Curve Point 28 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.28.xVal | 0 | AO303 | Curve
AI388 | Curve Point 28 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.28.yVal | 0 | AO304 | Curve
AI389 | Curve Point 29 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.29.xVal | 0 | AO305 | Curve
AI390 | Curve Point 29 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.29.yVal | 0 | AO306 | Curve
AI391 | Curve Point 30 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.30.xVal | 0 | AO307 | Curve
AI392 | Curve Point 30 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.30.yVal | 0 | AO308 | Curve
AI393 | Curve Point 31 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.31.xVal | 0 | AO309 | Curve
AI394 | Curve Point 31 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.31.yVal | 0 | AO310 | Curve
AI395 | Curve Point 32 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.32.xVal | 0 | AO311 | Curve
AI396 | Curve Point 32 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.32.yVal | 0 | AO312 | Curve
AI397 | Curve Point 33 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.33.xVal | 0 | AO313 | Curve
AI398 | Curve Point 33 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.33.yVal | 0 | AO314 | Curve
AI399 | Curve Point 34 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.34.xVal | 0 | AO315 | Curve
AI400 | Curve Point 34 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.34.yVal | 0 | AO316 | Curve
AI401 | Curve Point 35 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.35.xVal | 0 | AO317 | Curve
AI402 | Curve Point 35 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.35.yVal | 0 | AO318 | Curve
AI403 | Curve Point 36 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.36.xVal | 0 | AO319 | Curve
AI404 | Curve Point 36 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.36.yVal | 0 | AO320 | Curve
AI405 | Curve Point 37 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.37.xVal | 0 | AO321 | Curve
AI406 | Curve Point 37 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.37.yVal | 0 | AO322 | Curve
AI407 | Curve Point 38 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.38.xVal | 0 | AO323 | Curve
AI408 | Curve Point 38 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.38.yVal | 0 | AO324 | Curve
AI409 | Curve Point 39 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.39.xVal | 0 | AO325 | Curve
AI410 | Curve Point 39 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.39.yVal | 0 | AO326 | Curve
AI411 | Curve Point 40 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.40.xVal | 0 | AO327 | Curve
AI412 | Curve Point 40 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.40.yVal | 0 | AO328 | Curve
AI413 | Curve Point 41 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.41.xVal | 0 | AO329 | Curve
AI414 | Curve Point 41 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.41.yVal | 0 | AO330 | Curve
AI415 | Curve Point 42 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.42.xVal | 0 | AO331 | Curve
AI416 | Curve Point 42 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.42.yVal | 0 | AO332 | Curve
AI417 | Curve Point 43 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.43.xVal | 0 | AO333 | Curve
AI418 | Curve Point 43 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.43.yVal | 0 | AO334 | Curve
AI419 | Curve Point 44 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.44.xVal | 0 | AO335 | Curve
AI420 | Curve Point 44 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.44.yVal | 0 | AO336 | Curve
AI421 | Curve Point 45 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.45.xVal | 0 | AO337 | Curve
AI422 | Curve Point 45 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.45.yVal | 0 | AO338 | Curve
AI423 | Curve Point 46 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.46.xVal | 0 | AO339 | Curve
AI424 | Curve Point 46 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.46.yVal | 0 | AO340 | Curve
AI425 | Curve Point 47 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.47.xVal | 0 | AO341 | Curve
AI426 | Curve Point 47 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.47.yVal | 0 | AO342 | Curve
AI427 | Curve Point 48 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.48.xVal | 0 | AO343 | Curve
AI428 | Curve Point 48 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.48.yVal | 0 | AO344 | Curve
AI429 | Curve Point 49 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.49.xVal | 0 | AO345 | Curve
AI430 | Curve Point 49 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.49.yVal | 0 | AO346 | Curve
AI431 | Curve Point 50 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.50.xVal | 0 | AO347 | Curve
AI432 | Curve Point 50 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.50.yVal | 0 | AO348 | Curve
AI433 | Curve Point 51 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.51.xVal | 0 | AO349 | Curve
AI434 | Curve Point 51 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.51.yVal | 0 | AO350 | Curve
AI435 | Curve Point 52 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.52.xVal | 0 | AO351 | Curve
AI436 | Curve Point 52 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.52.yVal | 0 | AO352 | Curve
AI437 | Curve Point 53 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.53.xVal | 0 | AO353 | Curve
AI438 | Curve Point 53 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.53.yVal | 0 | AO354 | Curve
AI439 | Curve Point 54 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.54.xVal | 0 | AO355 | Curve
AI440 | Curve Point 54 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.54.yVal | 0 | AO356 | Curve
AI441 | Curve Point 55 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.55.xVal | 0 | AO357 | Curve
AI442 | Curve Point 55 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.55.yVal | 0 | AO358 | Curve
AI443 | Curve Point 56 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.56.xVal | 0 | AO359 | Curve
AI444 | Curve Point 56 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.56.yVal | 0 | AO360 | Curve
AI445 | Curve Point 57 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.57.xVal | 0 | AO361 | Curve
AI446 | Curve Point 57 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.57.yVal | 0 | AO362 | Curve
AI447 | Curve Point 58 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.58.xVal | 0 | AO363 | Curve
AI448 | Curve Point 58 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.58.yVal | 0 | AO364 | Curve
AI449 | Curve Point 59 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.59.xVal | 0 | AO365 | Curve
AI450 | Curve Point 59 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.59.yVal | 0 | AO366 | Curve
AI451 | Curve Point 60 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.60.xVal | 0 | AO367 | Curve
AI452 | Curve Point 60 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.60.yVal | 0 | AO368 | Curve
AI453 | Curve Point 61 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.61.xVal | 0 | AO369 | Curve
AI454 | Curve Point 61 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.61.yVal | 0 | AO370 | Curve
AI455 | Curve Point 62 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.62.xVal | 0 | AO371 | Curve
AI456 | Curve Point 62 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.62.yVal | 0 | AO372 | Curve
AI457 | Curve Point 63 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.63.xVal | 0 | AO373 | Curve
AI458 | Curve Point 63 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.63.yVal | 0 | AO374 | Curve
AI459 | Curve Point 64 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.64.xVal | 0 | AO375 | Curve
AI460 | Curve Point 64 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.64.yVal | 0 | AO376 | Curve
AI461 | Curve Point 65 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.65.xVal | 0 | AO377 | Curve
AI462 | Curve Point 65 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.65.yVal | 0 | AO378 | Curve
AI463 | Curve Point 66 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.66.xVal | 0 | AO379 | Curve
AI464 | Curve Point 66 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.66.yVal | 0 | AO380 | Curve
AI465 | Curve Point 67 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.67.xVal | 0 | AO381 | Curve
AI466 | Curve Point 67 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.67.yVal | 0 | AO382 | Curve
AI467 | Curve Point 68 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.68.xVal | 0 | AO383 | Curve
AI468 | Curve Point 68 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.68.yVal | 0 | AO384 | Curve
AI469 | Curve Point 69 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.69.xVal | 0 | AO385 | Curve
AI470 | Curve Point 69 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.69.yVal | 0 | AO386 | Curve
AI471 | Curve Point 70 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.70.xVal | 0 | AO387 | Curve
AI472 | Curve Point 70 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.70.yVal | 0 | AO388 | Curve
AI473 | Curve Point 71 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.71.xVal | 0 | AO389 | Curve
AI474 | Curve Point 71 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.71.yVal | 0 | AO390 | Curve
AI475 | Curve Point 72 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.72.xVal | 0 | AO391 | Curve
AI476 | Curve Point 72 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.72.yVal | 0 | AO392 | Curve
AI477 | Curve Point 73 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.73.xVal | 0 | AO393 | Curve
AI478 | Curve Point 73 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.73.yVal | 0 | AO394 | Curve
AI479 | Curve Point 74 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.74.xVal | 0 | AO395 | Curve
AI480 | Curve Point 74 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.74.yVal | 0 | AO396 | Curve
AI481 | Curve Point 75 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.75.xVal | 0 | AO397 | Curve
AI482 | Curve Point 75 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.75.yVal | 0 | AO398 | Curve
AI483 | Curve Point 76 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.76.xVal | 0 | AO399 | Curve
AI484 | Curve Point 76 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.76.yVal | 0 | AO400 | Curve
AI485 | Curve Point 77 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.77.xVal | 0 | AO401 | Curve
AI486 | Curve Point 77 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.77.yVal | 0 | AO402 | Curve
AI487 | Curve Point 78 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.78.xVal | 0 | AO403 | Curve
AI488 | Curve Point 78 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.78.yVal | 0 | AO404 | Curve
AI489 | Curve Point 79 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.79.xVal | 0 | AO405 | Curve
AI490 | Curve Point 79 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.79.yVal | 0 | AO406 | Curve
AI491 | Curve Point 80 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.80.xVal | 0 | AO407 | Curve
AI492 | Curve Point 80 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.80.yVal | 0 | AO408 | Curve
AI493 | Curve Point 81 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.81.xVal | 0 | AO409 | Curve
AI494 | Curve Point 81 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.81.yVal | 0 | AO410 | Curve
AI495 | Curve Point 82 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.82.xVal | 0 | AO411 | Curve
AI496 | Curve Point 82 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.82.yVal | 0 | AO412 | Curve
AI497 | Curve Point 83 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.83.xVal | 0 | AO413 | Curve
AI498 | Curve Point 83 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.83.yVal | 0 | AO414 | Curve
AI499 | Curve Point 84 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.84.xVal | 0 | AO415 | Curve
AI500 | Curve Point 84 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.84.yVal | 0 | AO416 | Curve
AI501 | Curve Point 85 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.85.xVal | 0 | AO417 | Curve
AI502 | Curve Point 85 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.85.yVal | 0 | AO418 | Curve
AI503 | Curve Point 86 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.86.xVal | 0 | AO419 | Curve
AI504 | Curve Point 86 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.86.yVal | 0 | AO420 | Curve
AI505 | Curve Point 87 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.87.xVal | 0 | AO421 | Curve
AI506 | Curve Point 87 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.87.yVal | 0 | AO422 | Curve
AI507 | Curve Point 88 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.88.xVal | 0 | AO423 | Curve
AI508 | Curve Point 88 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.88.yVal | 0 | AO424 | Curve
AI509 | Curve Point 89 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.89.xVal | 0 | AO425 | Curve
AI510 | Curve Point 89 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.89.yVal | 0 | AO426 | Curve
AI511 | Curve Point 90 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.90.xVal | 0 | AO427 | Curve
AI512 | Curve Point 90 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.90.yVal | 0 | AO428 | Curve
AI513 | Curve Point 91 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.91.xVal | 0 | AO429 | Curve
AI514 | Curve Point 91 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.91.yVal | 0 | AO430 | Curve
AI515 | Curve Point 92 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.92.xVal | 0 | AO431 | Curve
AI516 | Curve Point 92 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.92.yVal | 0 | AO432 | Curve
AI517 | Curve Point 93 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.93.xVal | 0 | AO433 | Curve
AI518 | Curve Point 93 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.93.yVal | 0 | AO434 | Curve
AI519 | Curve Point 94 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.94.xVal | 0 | AO435 | Curve
AI520 | Curve Point 94 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.94.yVal | 0 | AO436 | Curve
AI521 | Curve Point 95 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.95.xVal | 0 | AO437 | Curve
AI522 | Curve Point 95 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.95.yVal | 0 | AO438 | Curve
AI523 | Curve Point 96 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.96.xVal | 0 | AO439 | Curve
AI524 | Curve Point 96 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.96.yVal | 0 | AO440 | Curve
AI525 | Curve Point 97 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.97.xVal | 0 | AO441 | Curve
AI526 | Curve Point 97 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.97.yVal | 0 | AO442 | Curve
AI527 | Curve Point 98 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.98.xVal | 0 | AO443 | Curve
AI528 | Curve Point 98 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.98.yVal | 0 | AO444 | Curve
AI529 | Curve Point 99 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.99.xVal | 0 | AO445 | Curve
AI530 | Curve Point 99 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.99.yVal | 0 | AO446 | Curve
AI531 | Curve Point 100 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.100.xVal | 0 | AO447 | Curve
AI532 | Curve Point 100 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.100.yVal | 0 | AO448 | Curve
AI533 | System Meter Type of Connection Point. Enumeration: <0> unknown, <1> DER to local EPS <2> Internal to DER <3> local EPS with load to area EPS (PCC with load) <4> local EPS w/o load to area EPS (PCC without load) <5> Load to local EPS <6> External to DER beyond the PCC <7> External to DER within the local EPS <8> Auxiliary DER Load <9> Group of DERs to the area EPS <99> Other | 3 | 0 | 99 | 1 | 0 | Enum | DECP.EcpConnType | 0 |  | Monitoring | M
AI534 | System Meter Type of Circuit Phases. Enumeration: <0> unknown <1> Single phase <2> Split phase <3> 2-phase <4> 3-phase delta <5> 3-phase wye <6> 3-phase wye grounded <7> 3-phase / 3-wire (inverter type) <8> 3-phase / 4-wire (inverter type) | 3 | 0 | 8 | 1 | 0 | Enum | DECP.PhsConnTyp | 0 |  | Monitoring | M
AI535 | System Meter Apparent Power Calculation Method. Calculation method for total apparent power calculation. Enumeration: <0> unknown <1> vector <2> aritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | SYS.MMXU.ClcTotVA | 0 |  | Monitoring | M
AI536 | System Meter Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | SYS.MMXU.Hz | 0 |  | Monitoring | M | M
AI537 | System Meter Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW | 0 |  | Monitoring | M | M
AI538 | System Meter Active Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.W.phsA.mag | 0 |  | Monitoring | M
AI539 | System Meter Active Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.W.phsB.mag | 0 |  | Monitoring | M
AI540 | System Meter Active Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.W.phsC.mag | 0 |  | Monitoring | M
AI541 | System Meter Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | SYS.MMXU.TotVAr | 0 |  | Monitoring | M | M
AI542 | System Meter Reactive Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Var | SYS.MMXU.Var.phsA.mag | 0 |  | Monitoring | M
AI543 | System Meter Reactive Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Var | SYS.MMXU.VAr.phsB.mag | 0 |  | Monitoring | M
AI544 | System Meter Reactive Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Var | SYS.MMXU.VAr.phsC.mag | 0 |  | Monitoring | M
AI545 | System Meter Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | SYS.MMXU.TotPF | 0 |  | Monitoring | M
AI546 | System Meter Apparent Power | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | SYS.MMXU.TotVA | 0 |  | Monitoring | M
AI547 | System Meter Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.mag | 0 |  | Monitoring | M | M
AI548 | System Meter Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsA.ang | 0 |  | Monitoring | M | M
AI549 | System Meter Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.mag | 0 |  | Monitoring | M | M
AI550 | System Meter Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsB.ang | 0 |  | Monitoring | M | M
AI551 | System Meter Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.mag | 0 |  | Monitoring | M | M
AI552 | System Meter Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsC.ang | 0 |  | Monitoring | M | M
AI553 | System Meter Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.AvPPVPhs | 0 |  | Monitoring | M | M
AI554 | System Meter Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsA.mag | 0 |  | Monitoring | M | M
AI555 | System Meter Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsB.mag | 0 |  | Monitoring | M | M
AI556 | System Meter Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsC.mag | 0 |  | Monitoring | M | M
AI557 | System Meter Active Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW.rangeC.hLim | 0 | AO449 | Monitoring | M
AI558 | System Meter Active Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW.rangeC.lLim | 0 | AO450 | Monitoring | M
AI559 | System Meter Reactive Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | var | SYS.MMXU.TotVAr.rangeC.hLim | 0 | AO451 | Monitoring | M
AI560 | System Meter Reactive Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | var | SYS.MMXU.TotVAr.rangeC.lLim | 0 | AO452 | Monitoring | M
AI561 | System Meter Power Factor – High Threshold | 3 | -100 | 100 | 0.01 | 0 | None | SYS.MMXU.TotPF.rangeC.hLim | 0 | AO453 | Monitoring | M
AI562 | System Meter Power Factor – Low Threshold | 3 | -100 | 100 | 0.01 | 0 | None | SYS.MMXU.TotPF.rangeC.lLim | 0 | AO454 | Monitoring | M
AI563 | System Meter Phase A Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.rangeC.hLim | 0 | AO455 | Monitoring | M
AI564 | System Meter Phase A Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.rangeC.lLim | 0 | AO456 | Monitoring | M
AI565 | System Meter Phase B Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.rangeC.hLim | 0 | AO457 | Monitoring | M
AI566 | System Meter Phase B Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.rangeC.lLim | 0 | AO458 | Monitoring | M
AI567 | System Meter Phase C Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.rangeC.hLim | 0 | AO459 | Monitoring | M
AI568 | System Meter Phase C Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.rangeC.lLim | 0 | AO460 | Monitoring | M
AI581 | Renewable energy source percent. Percentage of the active power currently generated which results from renewable energy resource. | 3 | 0 | 2147483647 | 1 | 0 | Percent Watts | DREN.RenWPct | 0 |  | Renewable energy source
AI582 | Renewable energy source. Max rated active power (WMaxRtg) which may result from renewable energy resource | 2 | 0 | 2147483647 | 1 | 0 | Watts | DREN.RenWMaxRtg | 0 | AO473 | Renewable energy source
AI583 | Charge/Discharge. Charge Discharge attempted output, based on the Watt input and other parameters. | 3 | 0 | 2147483647 | 1 | 0 | Watts | DWGC.ReqW | 0 |  | Charge/Discharge
AI584 | Max SOC for Active Power Following #1 (Peak Power Limiting) | 2 | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWMeteraxPct | 0 | AO474 | Peak Power Limiting
AI585 | Min SOC for Active Power Following #1 (Peak Power Limiting) | 2 | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWMeterinPct | 0 | AO475 | Peak Power Limiting
AI586 | Max SOC for Active Power Following #2 (Load Following) | 2 | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWMeteraxPct | 0 | AO476 | Load Following
AI587 | Min SOC for Active Power Following #2 (Load Following) | 2 | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWMeterinPct | 0 | AO477 | Load Following
AI588 | Max SOC for Active Power Following #3 (Generation Following) | 2 | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWMeteraxPct | 0 | AO478 | Generation Following
AI589 | Min SOC for Active Power Following #3 (Generation Following) | 2 | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWMeterinPct | 0 | AO479 | Generation Following
AI590 | Frequency-Watt Droop High Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | 0 | AO480 | Droop Freq-Watt | C: For Function | M
AI591 | Frequency-Watt Droop Low Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | 0 | AO481 | Droop Freq-Watt | C: For Function | M
AI592 | High Frequency-Watt Droop Minimum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | 0 | AO482 | Droop Freq-Watt | C: For Function | M
AI593 | Low Frequency-Watt Droop Maximum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | 0 | AO483 | Droop Freq-Watt | C: For Function | M
AI594 | Volt-Var, 4 V-Q pairs Volt V1 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPt1 | 0 | AO484 | Volt-Var | If Volt-Var curve selector = 0
AI595 | Volt-Var 4 V-Q pairs Vars Q1 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VarPt1 | 0 | AO485 | Volt-Var | If Volt-Var curve selector = 0
AI596 | Volt-Var 4 V-Q pairs Volt V2 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPt2 | 0 | AO486 | Volt-Var | If Volt-Var curve selector = 0
AI597 | Volt-Var 4 V-Q pairs Vars Q2 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VarPt2 | 0 | AO487 | Volt-Var | If Volt-Var curve selector = 0
AI598 | Volt-Var 4 V-Q pairs Volt V3 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPt3 | 0 | AO488 | Volt-Var | If Volt-Var curve selector = 0
AI599 | Volt-Var 4 V-Q pairs Vars Q3 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VarPt3 | 0 | AO489 | Volt-Var | If Volt-Var curve selector = 0
AI600 | Volt-Var 4 V-Q pairs Volt V4 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPt4 | 0 | AO490 | Volt-Var | If Volt-Var curve selector = 0
AI601 | Volt-Var 4 V-Q pairs Vars Q4 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VarPt4 | 0 | AO491 | Volt-Var | If Volt-Var curve selector = 0
AI602 | Watt-Var 4 P-Q pairs Watt P1 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPt1 | 0 | AO492 | Watt-Var | If Watt-Var curve selector = 0
AI603 | Watt-Var 4 P-Q pairs Vars Q1 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPt1 | 0 | AO493 | Watt-Var | If Watt-Var curve selector = 0
AI604 | Watt-Var 4 P-Q pairs Watt P2 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPt2 | 0 | AO494 | Watt-Var | If Watt-Var curve selector = 0
AI605 | Watt-Var 4 P-Q pairs Vars Q2 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPt2 | 0 | AO495 | Watt-Var | If Watt-Var curve selector = 0
AI606 | Watt-Var 4 P-Q pairs Watt P3 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPt3 | 0 | AO496 | Watt-Var | If Watt-Var curve selector = 0
AI607 | Watt-Var 4 P-Q pairs Vars Q3 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPt3 | 0 | AO497 | Watt-Var | If Watt-Var curve selector = 0
AI608 | Watt-Var 4 P-Q pairs Watt P4 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPt4 | 0 | AO498 | Watt-Var | If Watt-Var curve selector = 0
AI609 | Watt-Var 4 P-Q pairs Vars Q4 | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPt4 | 0 | AO499 | Watt-Var | If Watt-Var curve selector = 0
AI610 | Volt-Watt 2 V-P pairs Volt V1 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC1.VPt1 | 0 | AO500 | Volt-Watt | If Volt-Watt curve selector = 0
AI611 | Volt-Watt 2 V-P pairs Watt P1 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC1.WPt1 | 0 | AO501 | Volt-Watt | If Volt-Watt curve selector = 0
AI612 | Volt-Watt 2 V-P pairs Volt V2 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC1.VPt2 | 0 | AO502 | Volt-Watt | If Volt-Watt curve selector = 0
AI613 | Volt-Watt 2 V-P pairs Watt P2 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC1.WPt2 | 0 | AO503 | Volt-Watt | If Volt-Watt curve selector = 0
AI614 | Volt-Watt 2 V-P pairs Volt V3 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC1.VPt3 | 0 | AO504 | Volt-Watt | If Volt-Watt curve selector = 0
AI615 | Volt-Watt 2 V-P pairs Watt P3 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC1.WPt3 | 0 | AO505 | Volt-Watt | If Volt-Watt curve selector = 0
AI616 | Volt-Watt 2 V-P pairs Volt V4 | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC1.VPt4 | 0 | AO506 | Volt-Watt | If Volt-Watt curve selector = 0
AI617 | Volt-Watt 2 V-P pairs Watt P4 | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC1.WPt4 | 0 | AO507 | Volt-Watt | If Volt-Watt curve selector = 0
AI618 | Charge/Discharge. Watts instead of percent WMax | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWGC.GnWSpt | 0 | AO508 | Charge/Discharge | C: For Function If BI114=1
AI619 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | 0 | AO509 | Active Power Limit | C: For Function if BI113 = 1 | M
AI620 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | 0 | AO510 | Active Power Limit | C: For Function if BI113 = 1 | M
AI621 | Constant Vars using vars as unit | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | 0 | AO511 | Constant Vars | C: For Function if BI115 = 1 | M
AI622 | Counter units. ENUM 1 = WHr, 2 = kWhr, 3 = MWHr | 2 | 1 | 3 | 1 | 0 | Enum | MESA.Ctr.Units | 1 | AO600 | Counters
AI2000 | Running Schedule Index | 2 | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCC.ActSchdRef | 0 |  | BC Scheduling | C: For Back Comp
AI2001 | Schedule to Edit Selector (n) | 3 | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCC.Schd | 0 | AO2000 | BC Scheduling | C: For Back Comp
AI2002 | Selected Schedule Identity | 3 | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCCn.Schd | 0 | AO2001 | BC Scheduling | C: For Back Comp
AI2003 | Selected Schedule Priority | 3 | 1 | 2147483647 | 1 | 0 | n/a | BC.FSCHn.SchdPrio | 1 | AO2002 | BC Scheduling | C: For Back Comp
AI2004 | Selected Schedule Type. Enumeration: <1> Low/High Voltage Ride-Through – hi Must Trip <2> Low/High Voltage Ride-Through – Low Must Trip <3> Low/High Voltage Ride-Through – hi Momentary <4> Low/High Voltage Ride-Through – Lo Momentary <5> Low/High Frequency Ride-Through – hi Must Trip <6> Low/High Frequency Ride-Through – Lo Must Trip <7> Low/High Frequency Ride-Through – hi Momentary <8> Low/High Frequency Ride-Through – Low Momentary <9> Dynamic Reactive Current Support - On/Off <10> Dynamic Volt-Watt - On/Off <11> Frequency-Watt - On/Off <12> Active Power Limit - Charging <13> Active Power Limit - Discharging <14> Charge/Discharge - Percent of Maximum <15> Coordinated Charge/Discharge - SOC Target <16> Active Power Response #1 - On/Off <17> Active Power Response #2 - On/Off <18> Active Power Response #3 - On/Off <19> AGC – Watts <20> Active Power Smoothing - On/Off <21> Volt-Watt – Curve Index <22> Frequency-Watt Curve – Curve Index <23> Frequency-Watt Curve – High Hysteresis <24> Frequency-Watt Curve – Low Hysteresis <25> Constant VArs - Percent of Maximum <26> Constant Power Factor - Power Factor <27> Volt-VAr – Curve Index <28> Watt-VAr – Curve Index <29> Power Factor Correction - On/Off <30> Reserved - For pricing mode <31> Charge/Discharge - enable/disable <32> Coordinated Charge/Discharge - enable/disable <33> Active Power Limit - Discharging - enable/disable <34> Active Power Response #1 - Limit <35> Active Power Response #2 - Limit <36> Active Power Response #3 - Limit <37> AGC - enable/disable ... <100> Vendor-specific enumerations above | 3 | 0 | 50 | 1 | 0 | Enum | MESAn.SchdTyp | 0 | AO2003 | BC Scheduling | C: For Back Comp
AI2005 | Selected Schedule Start Date | 3 | 0 | 2147483647 | 1 | 0 | Days | BC.FSCHn.StrTm.Date | 0 | AO2004 | BC Scheduling | C: For Back Comp
AI2006 | Selected Schedule Start Time | 3 | 0 | 86400000 | 1 | 0 | Seconds | BC.FSCHn.StrTm.Time | 0 | AO2005 | BC Scheduling | C: For Back Comp
AI2007 | Selected Schedule Repeat Interval | 3 | 0 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.NxtStrTm | 0 | AO2006 | BC Scheduling | C: For Back Comp
AI2008 | Selected Schedule Repeat Interval Units | 3 | 0 | 8 | 1 | 0 | n/a | BC.FSCHn.SchdReuse | 0 | AO2007 | BC Scheduling | C: For Back Comp
AI2009 | Selected Schedule Validation Status | 3 | 0 | 5 | 1 | 0 | n/a | BC.FSCHn.SchdSt.1 | 0 |  | BC Scheduling | C: For Back Comp
AI2010 | Selected Schedule Status | 2 | 0 | 5 | 1 | 0 | Enum | BC.FSCHn.SchdSt.2 | 0 |  | BC Scheduling | C: For Back Comp
AI2011 | Selected Schedule Number of Points | 3 | 0 | 2147483647 | 1 | 0 | Integer | BC.FSCHn.NumEntr | 100 | AO2008 | BC Scheduling | C: For Back Comp
AI2012 | Selected Schedule Point [1] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.1 | 0 | AO2009 | BC Scheduling | C: For Back Comp
AI2013 | Selected Schedule Point [1] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.1 | 0 | AO2010 | BC Scheduling | C: For Back Comp
AI2014 | Selected Schedule Point [2] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.2 | 0 | AO2011 | BC Scheduling | C: For Back Comp
AI2015 | Selected Schedule Point [2] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.2 | 0 | AO2012 | BC Scheduling | C: For Back Comp
AI2016 | Selected Schedule Point [3] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.3 | 0 | AO2013 | BC Scheduling | C: For Back Comp
AI2017 | Selected Schedule Point [3] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.3 | 0 | AO2014 | BC Scheduling | C: For Back Comp
AI2018 | Selected Schedule Point [4] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.4 | 0 | AO2015 | BC Scheduling | C: For Back Comp
AI2019 | Selected Schedule Point [4] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.4 | 0 | AO2016 | BC Scheduling | C: For Back Comp
AI2020 | Selected Schedule Point [5] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.5 | 0 | AO2017 | BC Scheduling | C: For Back Comp
AI2021 | Selected Schedule Point [5] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.5 | 0 | AO2018 | BC Scheduling | C: For Back Comp
AI2022 | Selected Schedule Point [6] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.6 | 0 | AO2019 | BC Scheduling | C: For Back Comp
AI2023 | Selected Schedule Point [6] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.6 | 0 | AO2020 | BC Scheduling | C: For Back Comp
AI2024 | Selected Schedule Point [7] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.7 | 0 | AO2021 | BC Scheduling | C: For Back Comp
AI2025 | Selected Schedule Point [7] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.7 | 0 | AO2022 | BC Scheduling | C: For Back Comp
AI2026 | Selected Schedule Point [8] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.8 | 0 | AO2023 | BC Scheduling | C: For Back Comp
AI2027 | Selected Schedule Point [8] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.8 | 0 | AO2024 | BC Scheduling | C: For Back Comp
AI2028 | Selected Schedule Point [9] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.9 | 0 | AO2025 | BC Scheduling | C: For Back Comp
AI2029 | Selected Schedule Point [9] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.9 | 0 | AO2026 | BC Scheduling | C: For Back Comp
AI2030 | Selected Schedule Point [10] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.10 | 0 | AO2027 | BC Scheduling | C: For Back Comp
AI2031 | Selected Schedule Point [10] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.10 | 0 | AO2028 | BC Scheduling | C: For Back Comp
AI2032 | Selected Schedule Point [11] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.11 | 0 | AO2029 | BC Scheduling | C: For Back Comp
AI2033 | Selected Schedule Point [11] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.11 | 0 | AO2030 | BC Scheduling | C: For Back Comp
AI2034 | Selected Schedule Point [12] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.12 | 0 | AO2031 | BC Scheduling | C: For Back Comp
AI2035 | Selected Schedule Point [12] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.12 | 0 | AO2032 | BC Scheduling | C: For Back Comp
AI2036 | Selected Schedule Point [13] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.13 | 0 | AO2033 | BC Scheduling | C: For Back Comp
AI2037 | Selected Schedule Point [13] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.13 | 0 | AO2034 | BC Scheduling | C: For Back Comp
AI2038 | Selected Schedule Point [14] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.14 | 0 | AO2035 | BC Scheduling | C: For Back Comp
AI2039 | Selected Schedule Point [14] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.14 | 0 | AO2036 | BC Scheduling | C: For Back Comp
AI2040 | Selected Schedule Point [15] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.15 | 0 | AO2037 | BC Scheduling | C: For Back Comp
AI2041 | Selected Schedule Point [15] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.15 | 0 | AO2038 | BC Scheduling | C: For Back Comp
AI2042 | Selected Schedule Point [16] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.16 | 0 | AO2039 | BC Scheduling | C: For Back Comp
AI2043 | Selected Schedule Point [16] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.16 | 0 | AO2040 | BC Scheduling | C: For Back Comp
AI2044 | Selected Schedule Point [17] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.17 | 0 | AO2041 | BC Scheduling | C: For Back Comp
AI2045 | Selected Schedule Point [17] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.17 | 0 | AO2042 | BC Scheduling | C: For Back Comp
AI2046 | Selected Schedule Point [18] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.18 | 0 | AO2043 | BC Scheduling | C: For Back Comp
AI2047 | Selected Schedule Point [18] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.18 | 0 | AO2044 | BC Scheduling | C: For Back Comp
AI2048 | Selected Schedule Point [19] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.19 | 0 | AO2045 | BC Scheduling | C: For Back Comp
AI2049 | Selected Schedule Point [19] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.19 | 0 | AO2046 | BC Scheduling | C: For Back Comp
AI2050 | Selected Schedule Point [20] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.20 | 0 | AO2047 | BC Scheduling | C: For Back Comp
AI2051 | Selected Schedule Point [20] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.20 | 0 | AO2048 | BC Scheduling | C: For Back Comp
AI2052 | Selected Schedule Point [21] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.21 | 0 | AO2049 | BC Scheduling
AI2053 | Selected Schedule Point [21] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.21 | 0 | AO2050 | BC Scheduling
AI2054 | Selected Schedule Point [22] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.22 | 0 | AO2051 | BC Scheduling
AI2055 | Selected Schedule Point [22] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.22 | 0 | AO2052 | BC Scheduling
AI2056 | Selected Schedule Point [23] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.23 | 0 | AO2053 | BC Scheduling
AI2057 | Selected Schedule Point [23] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.23 | 0 | AO2054 | BC Scheduling
AI2058 | Selected Schedule Point [24] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.24 | 0 | AO2055 | BC Scheduling
AI2059 | Selected Schedule Point [24] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.24 | 0 | AO2056 | BC Scheduling
AI2060 | Selected Schedule Point [25] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.25 | 0 | AO2057 | BC Scheduling
AI2061 | Selected Schedule Point [25] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.25 | 0 | AO2058 | BC Scheduling
AI2062 | Selected Schedule Point [26] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.26 | 0 | AO2059 | BC Scheduling
AI2063 | Selected Schedule Point [26] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.26 | 0 | AO2060 | BC Scheduling
AI2064 | Selected Schedule Point [27] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.27 | 0 | AO2061 | BC Scheduling
AI2065 | Selected Schedule Point [27] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.27 | 0 | AO2062 | BC Scheduling
AI2066 | Selected Schedule Point [28] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.28 | 0 | AO2063 | BC Scheduling
AI2067 | Selected Schedule Point [28] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.28 | 0 | AO2064 | BC Scheduling
AI2068 | Selected Schedule Point [29] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.29 | 0 | AO2065 | BC Scheduling
AI2069 | Selected Schedule Point [29] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.29 | 0 | AO2066 | BC Scheduling
AI2070 | Selected Schedule Point [30] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.30 | 0 | AO2067 | BC Scheduling
AI2071 | Selected Schedule Point [30] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.30 | 0 | AO2068 | BC Scheduling
AI2072 | Selected Schedule Point [31] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.31 | 0 | AO2069 | BC Scheduling
AI2073 | Selected Schedule Point [31] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.31 | 0 | AO2070 | BC Scheduling
AI2074 | Selected Schedule Point [32] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.32 | 0 | AO2071 | BC Scheduling
AI2075 | Selected Schedule Point [32] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.32 | 0 | AO2072 | BC Scheduling
AI2076 | Selected Schedule Point [33] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.33 | 0 | AO2073 | BC Scheduling
AI2077 | Selected Schedule Point [33] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.33 | 0 | AO2074 | BC Scheduling
AI2078 | Selected Schedule Point [34] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.34 | 0 | AO2075 | BC Scheduling
AI2079 | Selected Schedule Point [34] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.34 | 0 | AO2076 | BC Scheduling
AI2080 | Selected Schedule Point [35] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.35 | 0 | AO2077 | BC Scheduling
AI2081 | Selected Schedule Point [35] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.35 | 0 | AO2078 | BC Scheduling
AI2082 | Selected Schedule Point [36] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.36 | 0 | AO2079 | BC Scheduling
AI2083 | Selected Schedule Point [36] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.36 | 0 | AO2080 | BC Scheduling
AI2084 | Selected Schedule Point [37] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.37 | 0 | AO2081 | BC Scheduling
AI2085 | Selected Schedule Point [37] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.37 | 0 | AO2082 | BC Scheduling
AI2086 | Selected Schedule Point [38] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.38 | 0 | AO2083 | BC Scheduling
AI2087 | Selected Schedule Point [38] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.38 | 0 | AO2084 | BC Scheduling
AI2088 | Selected Schedule Point [39] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.39 | 0 | AO2085 | BC Scheduling
AI2089 | Selected Schedule Point [39] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.39 | 0 | AO2086 | BC Scheduling
AI2090 | Selected Schedule Point [40] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.40 | 0 | AO2087 | BC Scheduling
AI2091 | Selected Schedule Point [40] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.40 | 0 | AO2088 | BC Scheduling
AI2092 | Selected Schedule Point [41] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.41 | 0 | AO2089 | BC Scheduling
AI2093 | Selected Schedule Point [41] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.41 | 0 | AO2090 | BC Scheduling
AI2094 | Selected Schedule Point [42] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.42 | 0 | AO2091 | BC Scheduling
AI2095 | Selected Schedule Point [42] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.42 | 0 | AO2092 | BC Scheduling
AI2096 | Selected Schedule Point [43] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.43 | 0 | AO2093 | BC Scheduling
AI2097 | Selected Schedule Point [43] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.43 | 0 | AO2094 | BC Scheduling
AI2098 | Selected Schedule Point [44] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.44 | 0 | AO2095 | BC Scheduling
AI2099 | Selected Schedule Point [44] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.44 | 0 | AO2096 | BC Scheduling
AI2100 | Selected Schedule Point [45] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.45 | 0 | AO2097 | BC Scheduling
AI2101 | Selected Schedule Point [45] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.45 | 0 | AO2098 | BC Scheduling
AI2102 | Selected Schedule Point [46] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.46 | 0 | AO2099 | BC Scheduling
AI2103 | Selected Schedule Point [46] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.46 | 0 | AO2100 | BC Scheduling
AI2104 | Selected Schedule Point [47] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.47 | 0 | AO2101 | BC Scheduling
AI2105 | Selected Schedule Point [47] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.47 | 0 | AO2102 | BC Scheduling
AI2106 | Selected Schedule Point [48] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.48 | 0 | AO2103 | BC Scheduling
AI2107 | Selected Schedule Point [48] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.48 | 0 | AO2104 | BC Scheduling
AI2108 | Selected Schedule Point [49] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.49 | 0 | AO2105 | BC Scheduling
AI2109 | Selected Schedule Point [49] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.49 | 0 | AO2106 | BC Scheduling
AI2110 | Selected Schedule Point [50] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.50 | 0 | AO2107 | BC Scheduling
AI2111 | Selected Schedule Point [50] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.50 | 0 | AO2108 | BC Scheduling
AI2112 | Selected Schedule Point [51] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.51 | 0 | AO2109 | BC Scheduling
AI2113 | Selected Schedule Point [51] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.51 | 0 | AO2110 | BC Scheduling
AI2114 | Selected Schedule Point [52] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.52 | 0 | AO2111 | BC Scheduling
AI2115 | Selected Schedule Point [52] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.52 | 0 | AO2112 | BC Scheduling
AI2116 | Selected Schedule Point [53] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.53 | 0 | AO2113 | BC Scheduling
AI2117 | Selected Schedule Point [53] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.53 | 0 | AO2114 | BC Scheduling
AI2118 | Selected Schedule Point [54] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.54 | 0 | AO2115 | BC Scheduling
AI2119 | Selected Schedule Point [54] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.54 | 0 | AO2116 | BC Scheduling
AI2120 | Selected Schedule Point [55] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.55 | 0 | AO2117 | BC Scheduling
AI2121 | Selected Schedule Point [55] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.55 | 0 | AO2118 | BC Scheduling
AI2122 | Selected Schedule Point [56] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.56 | 0 | AO2119 | BC Scheduling
AI2123 | Selected Schedule Point [56] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.56 | 0 | AO2120 | BC Scheduling
AI2124 | Selected Schedule Point [57] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.57 | 0 | AO2121 | BC Scheduling
AI2125 | Selected Schedule Point [57] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.57 | 0 | AO2122 | BC Scheduling
AI2126 | Selected Schedule Point [58] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.58 | 0 | AO2123 | BC Scheduling
AI2127 | Selected Schedule Point [58] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.58 | 0 | AO2124 | BC Scheduling
AI2128 | Selected Schedule Point [59] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.59 | 0 | AO2125 | BC Scheduling
AI2129 | Selected Schedule Point [59] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.59 | 0 | AO2126 | BC Scheduling
AI2130 | Selected Schedule Point [60] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.60 | 0 | AO2127 | BC Scheduling
AI2131 | Selected Schedule Point [60] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.60 | 0 | AO2128 | BC Scheduling
AI2132 | Selected Schedule Point [61] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.61 | 0 | AO2129 | BC Scheduling
AI2133 | Selected Schedule Point [61] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.61 | 0 | AO2130 | BC Scheduling
AI2134 | Selected Schedule Point [62] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.62 | 0 | AO2131 | BC Scheduling
AI2135 | Selected Schedule Point [62] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.62 | 0 | AO2132 | BC Scheduling
AI2136 | Selected Schedule Point [63] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.63 | 0 | AO2133 | BC Scheduling
AI2137 | Selected Schedule Point [63] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.63 | 0 | AO2134 | BC Scheduling
AI2138 | Selected Schedule Point [64] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.64 | 0 | AO2135 | BC Scheduling
AI2139 | Selected Schedule Point [64] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.64 | 0 | AO2136 | BC Scheduling
AI2140 | Selected Schedule Point [65] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.65 | 0 | AO2137 | BC Scheduling
AI2141 | Selected Schedule Point [65] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.65 | 0 | AO2138 | BC Scheduling
AI2142 | Selected Schedule Point [66] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.66 | 0 | AO2139 | BC Scheduling
AI2143 | Selected Schedule Point [66] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.66 | 0 | AO2140 | BC Scheduling
AI2144 | Selected Schedule Point [67] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.67 | 0 | AO2141 | BC Scheduling
AI2145 | Selected Schedule Point [67] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.67 | 0 | AO2142 | BC Scheduling
AI2146 | Selected Schedule Point [68] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.68 | 0 | AO2143 | BC Scheduling
AI2147 | Selected Schedule Point [68] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.68 | 0 | AO2144 | BC Scheduling
AI2148 | Selected Schedule Point [69] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.69 | 0 | AO2145 | BC Scheduling
AI2149 | Selected Schedule Point [69] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.69 | 0 | AO2146 | BC Scheduling
AI2150 | Selected Schedule Point [70] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.70 | 0 | AO2147 | BC Scheduling
AI2151 | Selected Schedule Point [70] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.70 | 0 | AO2148 | BC Scheduling
AI2152 | Selected Schedule Point [71] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.71 | 0 | AO2149 | BC Scheduling
AI2153 | Selected Schedule Point [71] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.71 | 0 | AO2150 | BC Scheduling
AI2154 | Selected Schedule Point [72] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.72 | 0 | AO2151 | BC Scheduling
AI2155 | Selected Schedule Point [72] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.72 | 0 | AO2152 | BC Scheduling
AI2156 | Selected Schedule Point [73] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.73 | 0 | AO2153 | BC Scheduling
AI2157 | Selected Schedule Point [73] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.73 | 0 | AO2154 | BC Scheduling
AI2158 | Selected Schedule Point [74] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.74 | 0 | AO2155 | BC Scheduling
AI2159 | Selected Schedule Point [74] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.74 | 0 | AO2156 | BC Scheduling
AI2160 | Selected Schedule Point [75] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.75 | 0 | AO2157 | BC Scheduling
AI2161 | Selected Schedule Point [75] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.75 | 0 | AO2158 | BC Scheduling
AI2162 | Selected Schedule Point [76] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.76 | 0 | AO2159 | BC Scheduling
AI2163 | Selected Schedule Point [76] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.76 | 0 | AO2160 | BC Scheduling
AI2164 | Selected Schedule Point [77] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.77 | 0 | AO2161 | BC Scheduling
AI2165 | Selected Schedule Point [77] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.77 | 0 | AO2162 | BC Scheduling
AI2166 | Selected Schedule Point [78] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.78 | 0 | AO2163 | BC Scheduling
AI2167 | Selected Schedule Point [78] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.78 | 0 | AO2164 | BC Scheduling
AI2168 | Selected Schedule Point [79] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.79 | 0 | AO2165 | BC Scheduling
AI2169 | Selected Schedule Point [79] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.79 | 0 | AO2166 | BC Scheduling
AI2170 | Selected Schedule Point [80] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.80 | 0 | AO2167 | BC Scheduling
AI2171 | Selected Schedule Point [80] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.80 | 0 | AO2168 | BC Scheduling
AI2172 | Selected Schedule Point [81] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.81 | 0 | AO2169 | BC Scheduling
AI2173 | Selected Schedule Point [81] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.81 | 0 | AO2170 | BC Scheduling
AI2174 | Selected Schedule Point [82] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.82 | 0 | AO2171 | BC Scheduling
AI2175 | Selected Schedule Point [82] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.82 | 0 | AO2172 | BC Scheduling
AI2176 | Selected Schedule Point [83] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.83 | 0 | AO2173 | BC Scheduling
AI2177 | Selected Schedule Point [83] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.83 | 0 | AO2174 | BC Scheduling
AI2178 | Selected Schedule Point [84] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.84 | 0 | AO2175 | BC Scheduling
AI2179 | Selected Schedule Point [84] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.84 | 0 | AO2176 | BC Scheduling
AI2180 | Selected Schedule Point [85] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.85 | 0 | AO2177 | BC Scheduling
AI2181 | Selected Schedule Point [85] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.85 | 0 | AO2178 | BC Scheduling
AI2182 | Selected Schedule Point [86] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.86 | 0 | AO2179 | BC Scheduling
AI2183 | Selected Schedule Point [86] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.86 | 0 | AO2180 | BC Scheduling
AI2184 | Selected Schedule Point [87] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.87 | 0 | AO2181 | BC Scheduling
AI2185 | Selected Schedule Point [87] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.87 | 0 | AO2182 | BC Scheduling
AI2186 | Selected Schedule Point [88] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.88 | 0 | AO2183 | BC Scheduling
AI2187 | Selected Schedule Point [88] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.88 | 0 | AO2184 | BC Scheduling
AI2188 | Selected Schedule Point [89] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.89 | 0 | AO2185 | BC Scheduling
AI2189 | Selected Schedule Point [89] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.89 | 0 | AO2186 | BC Scheduling
AI2190 | Selected Schedule Point [90] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.90 | 0 | AO2187 | BC Scheduling
AI2191 | Selected Schedule Point [90] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.90 | 0 | AO2188 | BC Scheduling
AI2192 | Selected Schedule Point [91] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.91 | 0 | AO2189 | BC Scheduling
AI2193 | Selected Schedule Point [91] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.91 | 0 | AO2190 | BC Scheduling
AI2194 | Selected Schedule Point [92] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.92 | 0 | AO2191 | BC Scheduling
AI2195 | Selected Schedule Point [92] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.92 | 0 | AO2192 | BC Scheduling
AI2196 | Selected Schedule Point [93] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.93 | 0 | AO2193 | BC Scheduling
AI2197 | Selected Schedule Point [93] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.93 | 0 | AO2194 | BC Scheduling
AI2198 | Selected Schedule Point [94] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.94 | 0 | AO2195 | BC Scheduling
AI2199 | Selected Schedule Point [94] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.94 | 0 | AO2196 | BC Scheduling
AI2200 | Selected Schedule Point [95] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.95 | 0 | AO2197 | BC Scheduling
AI2201 | Selected Schedule Point [95] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.95 | 0 | AO2198 | BC Scheduling
AI2202 | Selected Schedule Point [96] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.96 | 0 | AO2199 | BC Scheduling
AI2203 | Selected Schedule Point [96] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.96 | 0 | AO2200 | BC Scheduling
AI2204 | Selected Schedule Point [97] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.97 | 0 | AO2201 | BC Scheduling
AI2205 | Selected Schedule Point [97] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.97 | 0 | AO2202 | BC Scheduling
AI2206 | Selected Schedule Point [98] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.98 | 0 | AO2203 | BC Scheduling
AI2207 | Selected Schedule Point [98] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.98 | 0 | AO2204 | BC Scheduling
AI2208 | Selected Schedule Point [99] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.99 | 0 | AO2205 | BC Scheduling
AI2209 | Selected Schedule Point [99] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.99 | 0 | AO2206 | BC Scheduling
AI2210 | Selected Schedule Point [100] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.100 | 0 | AO2207 | BC Scheduling
AI2211 | Selected Schedule Point [100] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.100 | 0 | AO2208 | BC Scheduling
AI2300 | Schedule [1] Status Editing = 1; Validated = 2; Enabled = 3; Running = 4; | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH1.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2301 | Schedule [1] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH1.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2302 | Schedule [1] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH1.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2303 | Schedule [2] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH2.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2304 | Schedule [2] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH2.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2305 | Schedule [2] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH2.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2306 | Schedule [3] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH3.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2307 | Schedule [3] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH3.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2308 | Schedule [3] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH3.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2309 | Schedule [4] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH4.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2310 | Schedule [4] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH4.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2311 | Schedule [4] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH4.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2312 | Schedule [5] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH5.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2313 | Schedule [5] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH5.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2314 | Schedule [5] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH5.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2315 | Schedule [6] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH6.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2316 | Schedule [6] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH6.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2317 | Schedule [6] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH6.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2318 | Schedule [7] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH7.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2319 | Schedule [7] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH7.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2320 | Schedule [7] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH7.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2321 | Schedule [8] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH8.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2322 | Schedule [8] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH8.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2323 | Schedule [8] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH8.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2324 | Schedule [9] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH9.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2325 | Schedule [9] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH9.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2326 | Schedule [9] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH9.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2327 | Schedule [10] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH10.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2328 | Schedule [10] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH10.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2329 | Schedule [10] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH10.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2330 | Schedule [11] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH11.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2331 | Schedule [11] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH11.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2332 | Schedule [11] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH11.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2333 | Schedule [12] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH12.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2334 | Schedule [12] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH12.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2335 | Schedule [12] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH12.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2336 | Schedule [13] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH13.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2337 | Schedule [13] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH13.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2338 | Schedule [13] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH13.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2339 | Schedule [14] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH14.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2340 | Schedule [14] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH14.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2341 | Schedule [14] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH14.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2342 | Schedule [15] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH15.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2343 | Schedule [15] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH15.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2344 | Schedule [15] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH15.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2345 | Schedule [16] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH16.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2346 | Schedule [16] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH16.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2347 | Schedule [16] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH16.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2348 | Schedule [17] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH17.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2349 | Schedule [17] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH17.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2350 | Schedule [17] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH17.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2351 | Schedule [18] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH18.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2352 | Schedule [18] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH18.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2353 | Schedule [18] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH18.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2354 | Schedule [19] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH19.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2355 | Schedule [19] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH19.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2356 | Schedule [19] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH19.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2357 | Schedule [20] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH20.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2358 | Schedule [20] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH20.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2359 | Schedule [20] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH20.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2360 | Schedule [21] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH21.SchdSt | 0 |  | BC Scheduling
AI2361 | Schedule [21] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH21.SchdPrio | 1 |  | BC Scheduling
AI2362 | Schedule [21] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH21.ActStrTm | 0 |  | BC Scheduling
AI2363 | Schedule [22] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH22.SchdSt | 0 |  | BC Scheduling
AI2364 | Schedule [22] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH22.SchdPrio | 1 |  | BC Scheduling
AI2365 | Schedule [22] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH22.ActStrTm | 0 |  | BC Scheduling
AI2366 | Schedule [23] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH23.SchdSt | 0 |  | BC Scheduling
AI2367 | Schedule [23] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH23.SchdPrio | 1 |  | BC Scheduling
AI2368 | Schedule [23] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH23.ActStrTm | 0 |  | BC Scheduling
AI2369 | Schedule [24] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH24.SchdSt | 0 |  | BC Scheduling
AI2370 | Schedule [24] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH24.SchdPrio | 1 |  | BC Scheduling
AI2371 | Schedule [24] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH24.ActStrTm | 0 |  | BC Scheduling
AI2372 | Schedule [25] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH25.SchdSt | 0 |  | BC Scheduling
AI2373 | Schedule [25] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH25.SchdPrio | 1 |  | BC Scheduling
AI2374 | Schedule [25] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH25.ActStrTm | 0 |  | BC Scheduling
AI2375 | Schedule [26] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH26.SchdSt | 0 |  | BC Scheduling
AI2376 | Schedule [26] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH26.SchdPrio | 1 |  | BC Scheduling
AI2377 | Schedule [26] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH26.ActStrTm | 0 |  | BC Scheduling
AI2378 | Schedule [27] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH27.SchdSt | 0 |  | BC Scheduling
AI2379 | Schedule [27] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH27.SchdPrio | 1 |  | BC Scheduling
AI2380 | Schedule [27] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH27.ActStrTm | 0 |  | BC Scheduling
AI2381 | Schedule [28] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH28.SchdSt | 0 |  | BC Scheduling
AI2382 | Schedule [28] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH28.SchdPrio | 1 |  | BC Scheduling
AI2383 | Schedule [28] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH28.ActStrTm | 0 |  | BC Scheduling
AI2384 | Schedule [29] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH29.SchdSt | 0 |  | BC Scheduling
AI2385 | Schedule [29] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH29.SchdPrio | 1 |  | BC Scheduling
AI2386 | Schedule [29] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH29.ActStrTm | 0 |  | BC Scheduling
AI2387 | Schedule [30] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH30.SchdSt | 0 |  | BC Scheduling
AI2388 | Schedule [30] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH30.SchdPrio | 1 |  | BC Scheduling
AI2389 | Schedule [30] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH30.ActStrTm | 0 |  | BC Scheduling
AI2390 | Schedule [31] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH31.SchdSt | 0 |  | BC Scheduling
AI2391 | Schedule [31] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH31.SchdPrio | 1 |  | BC Scheduling
AI2392 | Schedule [31] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH31.ActStrTm | 0 |  | BC Scheduling
AI2393 | Schedule [32] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH32.SchdSt | 0 |  | BC Scheduling
AI2394 | Schedule [32] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH32.SchdPrio | 1 |  | BC Scheduling
AI2395 | Schedule [32] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH32.ActStrTm | 0 |  | BC Scheduling
AI2396 | Schedule [33] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH33.SchdSt | 0 |  | BC Scheduling
AI2397 | Schedule [33] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH33.SchdPrio | 1 |  | BC Scheduling
AI2398 | Schedule [33] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH33.ActStrTm | 0 |  | BC Scheduling
AI2399 | Schedule [34] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH34.SchdSt | 0 |  | BC Scheduling
AI2400 | Schedule [34] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH34.SchdPrio | 1 |  | BC Scheduling
AI2401 | Schedule [34] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH34.ActStrTm | 0 |  | BC Scheduling
AI2402 | Schedule [35] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH35.SchdSt | 0 |  | BC Scheduling
AI2403 | Schedule [35] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH35.SchdPrio | 1 |  | BC Scheduling
AI2404 | Schedule [35] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH35.ActStrTm | 0 |  | BC Scheduling
AI2405 | Schedule [36] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH36.SchdSt | 0 |  | BC Scheduling
AI2406 | Schedule [36] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH36.SchdPrio | 1 |  | BC Scheduling
AI2407 | Schedule [36] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH36.ActStrTm | 0 |  | BC Scheduling
AI2408 | Schedule [37] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH37.SchdSt | 0 |  | BC Scheduling
AI2409 | Schedule [37] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH37.SchdPrio | 1 |  | BC Scheduling
AI2410 | Schedule [37] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH37.ActStrTm | 0 |  | BC Scheduling
AI2411 | Schedule [38] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH38.SchdSt | 0 |  | BC Scheduling
AI2412 | Schedule [38] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH38.SchdPrio | 1 |  | BC Scheduling
AI2413 | Schedule [38] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH38.ActStrTm | 0 |  | BC Scheduling
AI2414 | Schedule [39] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH39.SchdSt | 0 |  | BC Scheduling
AI2415 | Schedule [39] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH39.SchdPrio | 1 |  | BC Scheduling
AI2416 | Schedule [39] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH39.ActStrTm | 0 |  | BC Scheduling
AI2417 | Schedule [40] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH40.SchdSt | 0 |  | BC Scheduling
AI2418 | Schedule [40] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH40.SchdPrio | 1 |  | BC Scheduling
AI2419 | Schedule [40] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH40.ActStrTm | 0 |  | BC Scheduling
AI2420 | Schedule [41] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH41.SchdSt | 0 |  | BC Scheduling
AI2421 | Schedule [41] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH41.SchdPrio | 1 |  | BC Scheduling
AI2422 | Schedule [41] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH41.ActStrTm | 0 |  | BC Scheduling
AI2423 | Schedule [42] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH42.SchdSt | 0 |  | BC Scheduling
AI2424 | Schedule [42] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH42.SchdPrio | 1 |  | BC Scheduling
AI2425 | Schedule [42] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH42.ActStrTm | 0 |  | BC Scheduling
AI2426 | Schedule [43] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH43.SchdSt | 0 |  | BC Scheduling
AI2427 | Schedule [43] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH43.SchdPrio | 1 |  | BC Scheduling
AI2428 | Schedule [43] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH43.ActStrTm | 0 |  | BC Scheduling
AI2429 | Schedule [44] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH44.SchdSt | 0 |  | BC Scheduling
AI2430 | Schedule [44] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH44.SchdPrio | 1 |  | BC Scheduling
AI2431 | Schedule [44] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH44.ActStrTm | 0 |  | BC Scheduling
AI2432 | Schedule [45] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH45.SchdSt | 0 |  | BC Scheduling
AI2433 | Schedule [45] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH45.SchdPrio | 1 |  | BC Scheduling
AI2434 | Schedule [45] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH45.ActStrTm | 0 |  | BC Scheduling
AI2435 | Schedule [46] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH46.SchdSt | 0 |  | BC Scheduling
AI2436 | Schedule [46] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH46.SchdPrio | 1 |  | BC Scheduling
AI2437 | Schedule [46] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH46.ActStrTm | 0 |  | BC Scheduling
AI2438 | Schedule [47] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH47.SchdSt | 0 |  | BC Scheduling
AI2439 | Schedule [47] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH47.SchdPrio | 1 |  | BC Scheduling
AI2440 | Schedule [47] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH47.ActStrTm | 0 |  | BC Scheduling
AI2441 | Schedule [48] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH48.SchdSt | 0 |  | BC Scheduling
AI2442 | Schedule [48] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH48.SchdPrio | 1 |  | BC Scheduling
AI2443 | Schedule [48] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH48.ActStrTm | 0 |  | BC Scheduling
AI2444 | Schedule [49] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH49.SchdSt | 0 |  | BC Scheduling
AI2445 | Schedule [49] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH49.SchdPrio | 1 |  | BC Scheduling
AI2446 | Schedule [49] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH49.ActStrTm | 0 |  | BC Scheduling
AI2447 | Schedule [50] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH50.SchdSt | 0 |  | BC Scheduling
AI2448 | Schedule [50] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH50.SchdPrio | 1 |  | BC Scheduling
AI2449 | Schedule [50] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH50.ActStrTm | 0 |  | BC Scheduling
AI2450 | Schedule [51] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH51.SchdSt | 0 |  | BC Scheduling
AI2451 | Schedule [51] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH51.SchdPrio | 1 |  | BC Scheduling
AI2452 | Schedule [51] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH51.ActStrTm | 0 |  | BC Scheduling
AI2453 | Schedule [52] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH52.SchdSt | 0 |  | BC Scheduling
AI2454 | Schedule [52] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH52.SchdPrio | 1 |  | BC Scheduling
AI2455 | Schedule [52] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH52.ActStrTm | 0 |  | BC Scheduling
AI2456 | Schedule [53] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH53.SchdSt | 0 |  | BC Scheduling
AI2457 | Schedule [53] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH53.SchdPrio | 1 |  | BC Scheduling
AI2458 | Schedule [53] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH53.ActStrTm | 0 |  | BC Scheduling
AI2459 | Schedule [54] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH54.SchdSt | 0 |  | BC Scheduling
AI2460 | Schedule [54] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH54.SchdPrio | 1 |  | BC Scheduling
AI2461 | Schedule [54] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH54.ActStrTm | 0 |  | BC Scheduling
AI2462 | Schedule [55] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH55.SchdSt | 0 |  | BC Scheduling
AI2463 | Schedule [55] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH55.SchdPrio | 1 |  | BC Scheduling
AI2464 | Schedule [55] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH55.ActStrTm | 0 |  | BC Scheduling
AI2465 | Schedule [56] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH56.SchdSt | 0 |  | BC Scheduling
AI2466 | Schedule [56] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH56.SchdPrio | 1 |  | BC Scheduling
AI2467 | Schedule [56] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH56.ActStrTm | 0 |  | BC Scheduling
AI2468 | Schedule [57] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH57.SchdSt | 0 |  | BC Scheduling
AI2469 | Schedule [57] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH57.SchdPrio | 1 |  | BC Scheduling
AI2470 | Schedule [57] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH57.ActStrTm | 0 |  | BC Scheduling
AI2471 | Schedule [58] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH58.SchdSt | 0 |  | BC Scheduling
AI2472 | Schedule [58] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH58.SchdPrio | 1 |  | BC Scheduling
AI2473 | Schedule [58] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH58.ActStrTm | 0 |  | BC Scheduling
AI2474 | Schedule [59] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH59.SchdSt | 0 |  | BC Scheduling
AI2475 | Schedule [59] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH59.SchdPrio | 1 |  | BC Scheduling
AI2476 | Schedule [59] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH59.ActStrTm | 0 |  | BC Scheduling
AI2477 | Schedule [60] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH60.SchdSt | 0 |  | BC Scheduling
AI2478 | Schedule [60] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH60.SchdPrio | 1 |  | BC Scheduling
AI2479 | Schedule [60] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH60.ActStrTm | 0 |  | BC Scheduling
AI2480 | Schedule [61] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH61.SchdSt | 0 |  | BC Scheduling
AI2481 | Schedule [61] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH61.SchdPrio | 1 |  | BC Scheduling
AI2482 | Schedule [61] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH61.ActStrTm | 0 |  | BC Scheduling
AI2483 | Schedule [62] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH62.SchdSt | 0 |  | BC Scheduling
AI2484 | Schedule [62] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH62.SchdPrio | 1 |  | BC Scheduling
AI2485 | Schedule [62] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH62.ActStrTm | 0 |  | BC Scheduling
AI2486 | Schedule [63] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH63.SchdSt | 0 |  | BC Scheduling
AI2487 | Schedule [63] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH63.SchdPrio | 1 |  | BC Scheduling
AI2488 | Schedule [63] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH63.ActStrTm | 0 |  | BC Scheduling
AI2489 | Schedule [64] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH64.SchdSt | 0 |  | BC Scheduling
AI2490 | Schedule [64] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH64.SchdPrio | 1 |  | BC Scheduling
AI2491 | Schedule [64] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH64.ActStrTm | 0 |  | BC Scheduling
AI2492 | Schedule [65] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH65.SchdSt | 0 |  | BC Scheduling
AI2493 | Schedule [65] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH65.SchdPrio | 1 |  | BC Scheduling
AI2494 | Schedule [65] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH65.ActStrTm | 0 |  | BC Scheduling
AI2495 | Schedule [66] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH66.SchdSt | 0 |  | BC Scheduling
AI2496 | Schedule [66] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH66.SchdPrio | 1 |  | BC Scheduling
AI2497 | Schedule [66] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH66.ActStrTm | 0 |  | BC Scheduling
AI2498 | Schedule [67] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH67.SchdSt | 0 |  | BC Scheduling
AI2499 | Schedule [67] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH67.SchdPrio | 1 |  | BC Scheduling
AI2500 | Schedule [67] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH67.ActStrTm | 0 |  | BC Scheduling
AI2501 | Schedule [68] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH68.SchdSt | 0 |  | BC Scheduling
AI2502 | Schedule [68] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH68.SchdPrio | 1 |  | BC Scheduling
AI2503 | Schedule [68] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH68.ActStrTm | 0 |  | BC Scheduling
AI2504 | Schedule [69] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH69.SchdSt | 0 |  | BC Scheduling
AI2505 | Schedule [69] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH69.SchdPrio | 1 |  | BC Scheduling
AI2506 | Schedule [69] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH69.ActStrTm | 0 |  | BC Scheduling
AI2507 | Schedule [70] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH70.SchdSt | 0 |  | BC Scheduling
AI2508 | Schedule [70] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH70.SchdPrio | 1 |  | BC Scheduling
AI2509 | Schedule [70] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH70.ActStrTm | 0 |  | BC Scheduling
AI2510 | Schedule [71] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH71.SchdSt | 0 |  | BC Scheduling
AI2511 | Schedule [71] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH71.SchdPrio | 1 |  | BC Scheduling
AI2512 | Schedule [71] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH71.ActStrTm | 0 |  | BC Scheduling
AI2513 | Schedule [72] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH72.SchdSt | 0 |  | BC Scheduling
AI2514 | Schedule [72] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH72.SchdPrio | 1 |  | BC Scheduling
AI2515 | Schedule [72] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH72.ActStrTm | 0 |  | BC Scheduling
AI2516 | Schedule [73] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH73.SchdSt | 0 |  | BC Scheduling
AI2517 | Schedule [73] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH73.SchdPrio | 1 |  | BC Scheduling
AI2518 | Schedule [73] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH73.ActStrTm | 0 |  | BC Scheduling
AI2519 | Schedule [74] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH74.SchdSt | 0 |  | BC Scheduling
AI2520 | Schedule [74] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH74.SchdPrio | 1 |  | BC Scheduling
AI2521 | Schedule [74] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH74.ActStrTm | 0 |  | BC Scheduling
AI2522 | Schedule [75] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH75.SchdSt | 0 |  | BC Scheduling
AI2523 | Schedule [75] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH75.SchdPrio | 1 |  | BC Scheduling
AI2524 | Schedule [75] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH75.ActStrTm | 0 |  | BC Scheduling
AI2525 | Schedule [76] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH76.SchdSt | 0 |  | BC Scheduling
AI2526 | Schedule [76] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH76.SchdPrio | 1 |  | BC Scheduling
AI2527 | Schedule [76] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH76.ActStrTm | 0 |  | BC Scheduling
AI2528 | Schedule [77] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH77.SchdSt | 0 |  | BC Scheduling
AI2529 | Schedule [77] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH77.SchdPrio | 1 |  | BC Scheduling
AI2530 | Schedule [77] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH77.ActStrTm | 0 |  | BC Scheduling
AI2531 | Schedule [78] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH78.SchdSt | 0 |  | BC Scheduling
AI2532 | Schedule [78] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH78.SchdPrio | 1 |  | BC Scheduling
AI2533 | Schedule [78] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH78.ActStrTm | 0 |  | BC Scheduling
AI2534 | Schedule [79] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH79.SchdSt | 0 |  | BC Scheduling
AI2535 | Schedule [79] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH79.SchdPrio | 1 |  | BC Scheduling
AI2536 | Schedule [79] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH79.ActStrTm | 0 |  | BC Scheduling
AI2537 | Schedule [80] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH80.SchdSt | 0 |  | BC Scheduling
AI2538 | Schedule [80] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH80.SchdPrio | 1 |  | BC Scheduling
AI2539 | Schedule [80] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH80.ActStrTm | 0 |  | BC Scheduling
AI2540 | Schedule [81] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH81.SchdSt | 0 |  | BC Scheduling
AI2541 | Schedule [81] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH81.SchdPrio | 1 |  | BC Scheduling
AI2542 | Schedule [81] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH81.ActStrTm | 0 |  | BC Scheduling
AI2543 | Schedule [82] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH82.SchdSt | 0 |  | BC Scheduling
AI2544 | Schedule [82] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH82.SchdPrio | 1 |  | BC Scheduling
AI2545 | Schedule [82] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH82.ActStrTm | 0 |  | BC Scheduling
AI2546 | Schedule [83] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH83.SchdSt | 0 |  | BC Scheduling
AI2547 | Schedule [83] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH83.SchdPrio | 1 |  | BC Scheduling
AI2548 | Schedule [83] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH83.ActStrTm | 0 |  | BC Scheduling
AI2549 | Schedule [84] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH84.SchdSt | 0 |  | BC Scheduling
AI2550 | Schedule [84] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH84.SchdPrio | 1 |  | BC Scheduling
AI2551 | Schedule [84] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH84.ActStrTm | 0 |  | BC Scheduling
AI2552 | Schedule [85] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH85.SchdSt | 0 |  | BC Scheduling
AI2553 | Schedule [85] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH85.SchdPrio | 1 |  | BC Scheduling
AI2554 | Schedule [85] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH85.ActStrTm | 0 |  | BC Scheduling
AI2555 | Schedule [86] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH86.SchdSt | 0 |  | BC Scheduling
AI2556 | Schedule [86] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH86.SchdPrio | 1 |  | BC Scheduling
AI2557 | Schedule [86] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH86.ActStrTm | 0 |  | BC Scheduling
AI2558 | Schedule [87] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH87.SchdSt | 0 |  | BC Scheduling
AI2559 | Schedule [87] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH87.SchdPrio | 1 |  | BC Scheduling
AI2560 | Schedule [87] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH87.ActStrTm | 0 |  | BC Scheduling
AI2561 | Schedule [88] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH88.SchdSt | 0 |  | BC Scheduling
AI2562 | Schedule [88] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH88.SchdPrio | 1 |  | BC Scheduling
AI2563 | Schedule [88] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH88.ActStrTm | 0 |  | BC Scheduling
AI2564 | Schedule [89] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH89.SchdSt | 0 |  | BC Scheduling
AI2565 | Schedule [89] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH89.SchdPrio | 1 |  | BC Scheduling
AI2566 | Schedule [89] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH89.ActStrTm | 0 |  | BC Scheduling
AI2567 | Schedule [90] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH90.SchdSt | 0 |  | BC Scheduling
AI2568 | Schedule [90] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH90.SchdPrio | 1 |  | BC Scheduling
AI2569 | Schedule [90] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH90.ActStrTm | 0 |  | BC Scheduling
AI2570 | Schedule [91] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH91.SchdSt | 0 |  | BC Scheduling
AI2571 | Schedule [91] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH91.SchdPrio | 1 |  | BC Scheduling
AI2572 | Schedule [91] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH91.ActStrTm | 0 |  | BC Scheduling
AI2573 | Schedule [92] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH92.SchdSt | 0 |  | BC Scheduling
AI2574 | Schedule [92] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH92.SchdPrio | 1 |  | BC Scheduling
AI2575 | Schedule [92] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH92.ActStrTm | 0 |  | BC Scheduling
AI2576 | Schedule [93] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH93.SchdSt | 0 |  | BC Scheduling
AI2577 | Schedule [93] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH93.SchdPrio | 1 |  | BC Scheduling
AI2578 | Schedule [93] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH93.ActStrTm | 0 |  | BC Scheduling
AI2579 | Schedule [94] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH94.SchdSt | 0 |  | BC Scheduling
AI2580 | Schedule [94] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH94.SchdPrio | 1 |  | BC Scheduling
AI2581 | Schedule [94] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH94.ActStrTm | 0 |  | BC Scheduling
AI2582 | Schedule [95] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH95.SchdSt | 0 |  | BC Scheduling
AI2583 | Schedule [95] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH95.SchdPrio | 1 |  | BC Scheduling
AI2584 | Schedule [95] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH95.ActStrTm | 0 |  | BC Scheduling
AI2585 | Schedule [96] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH96.SchdSt | 0 |  | BC Scheduling
AI2586 | Schedule [96] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH96.SchdPrio | 1 |  | BC Scheduling
AI2587 | Schedule [96] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH96.ActStrTm | 0 |  | BC Scheduling
AI2588 | Schedule [97] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH97.SchdSt | 0 |  | BC Scheduling
AI2589 | Schedule [97] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH97.SchdPrio | 1 |  | BC Scheduling
AI2590 | Schedule [97] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH97.ActStrTm | 0 |  | BC Scheduling
AI2591 | Schedule [98] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH98.SchdSt | 0 |  | BC Scheduling
AI2592 | Schedule [98] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH98.SchdPrio | 1 |  | BC Scheduling
AI2593 | Schedule [98] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH98.ActStrTm | 0 |  | BC Scheduling
AI2594 | Schedule [99] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH99.SchdSt | 0 |  | BC Scheduling
AI2595 | Schedule [99] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH99.SchdPrio | 1 |  | BC Scheduling
AI2596 | Schedule [99] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH99.ActStrTm | 0 |  | BC Scheduling
AI2597 | Schedule [100] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH100.SchdSt | 0 |  | BC Scheduling
AI2598 | Schedule [100] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH100.SchdPrio | 1 |  | BC Scheduling
AI2599 | Schedule [100] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH100.ActStrTm | 0 |  | BC Scheduling
AI3000 | Schedule to Edit Selector (n) | 3 | 0 | 2147483647 | 1 | 0 | n/a | FSCC.Schd | 0 | AO3000 | Scheduling | C: For Sched
AI3001 | Selected Schedule Identity | 3 | 0 | 2147483647 | 1 | 0 | n/a | FSCCn.Schd | 0 | AO3001 | Scheduling | C: For Sched
AI3002 | Selected Schedule Priority | 3 | 1 | 2147483647 | 1 | 0 | n/a | FSCHn.SchdPrio | 1 | AO3002 | Scheduling | C: For Sched
AI3003 | Selected Schedule Start Date | 3 | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | 0 | AO3003 | Scheduling | C: For Sched
AI3004 | Selected Schedule Start Time | 3 | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | 0 | AO3004 | Scheduling | C: For Sched
AI3005 | Selected Schedule Stop Date | 3 | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | 0 | AO3005 | Scheduling | C: For Sched
AI3006 | Selected Schedule Stop Time | 3 | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | 0 | AO3006 | Scheduling | C: For Sched
AI3007 | Selected Schedule Repeat Interval | 3 | 0 | 2147483647 | 1 | 0 | Varies | FSCHn.NxtStrTm | 0 | AO3007 | Scheduling | C: For Sched
AI3008 | Selected Schedule Repeat Interval Units | 3 | 0 | 8 | 1 | 0 | n/a | FSCHn.SchdReuse | 0 | AO3008 | Scheduling | C: For Sched
AI3009 | Selected Schedule Validation State | 3 | 0 | 7 | 1 | 0 | n/a | FSCHn.SchdSt.1 | 0 |  | Scheduling | C: For Sched
AI3010 | Selected Schedule Status | 2 | 0 | 7 | 1 | 0 | Enum | FSCHn.SchdSt.2 | 0 |  | Scheduling | C: For Sched
AI3011 | Selected Schedule Number of Points | 3 | 0 | 2147483647 | 1 | 0 | Integer | FSCHn.NumEntr | 100 | AO3009 | Scheduling | C: For Sched
AI3012 | Selected Schedule Point [1] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.1 | 0 | AO3010 | Scheduling | C: For Sched
AI3013 | Selected Schedule Point [1] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.1 | 0 | AO3011 | Scheduling | C: For Sched
AI3014 | Selected Schedule Point [1] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.1 | 0 | AO3012 | Scheduling | C: For Sched
AI3015 | Selected Schedule Point [1] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.1 | 1 | AO3013 | Scheduling | C: For Sched
AI3016 | Selected Schedule Point [2] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.2 | 0 | AO3014 | Scheduling | C: For Sched
AI3017 | Selected Schedule Point [2] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.2 | 0 | AO3015 | Scheduling | C: For Sched
AI3018 | Selected Schedule Point [2] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.2 | 0 | AO3016 | Scheduling | C: For Sched
AI3019 | Selected Schedule Point [2] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.2 | 0 | AO3017 | Scheduling | C: For Sched
AI3020 | Selected Schedule Point [3] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.3 | 0 | AO3018 | Scheduling | C: For Sched
AI3021 | Selected Schedule Point [3] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.3 | 0 | AO3019 | Scheduling | C: For Sched
AI3022 | Selected Schedule Point [3] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.3 | 0 | AO3020 | Scheduling | C: For Sched
AI3023 | Selected Schedule Point [3] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.3 | 0 | AO3021 | Scheduling | C: For Sched
AI3024 | Selected Schedule Point [4] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.4 | 0 | AO3022 | Scheduling | C: For Sched
AI3025 | Selected Schedule Point [4] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.4 | 0 | AO3023 | Scheduling | C: For Sched
AI3026 | Selected Schedule Point [4] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.4 | 0 | AO3024 | Scheduling | C: For Sched
AI3027 | Selected Schedule Point [4] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.4 | 0 | AO3025 | Scheduling | C: For Sched
AI3028 | Selected Schedule Point [5] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.5 | 0 | AO3026 | Scheduling | C: For Sched
AI3029 | Selected Schedule Point [5] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.5 | 0 | AO3027 | Scheduling | C: For Sched
AI3030 | Selected Schedule Point [5] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.5 | 0 | AO3028 | Scheduling | C: For Sched
AI3031 | Selected Schedule Point [5] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.5 | 0 | AO3029 | Scheduling | C: For Sched
AI3032 | Selected Schedule Point [6] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.6 | 0 | AO3030 | Scheduling | C: For Sched
AI3033 | Selected Schedule Point [6] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.6 | 0 | AO3031 | Scheduling | C: For Sched
AI3034 | Selected Schedule Point [6] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.6 | 0 | AO3032 | Scheduling | C: For Sched
AI3035 | Selected Schedule Point [6] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.6 | 0 | AO3033 | Scheduling | C: For Sched
AI3036 | Selected Schedule Point [7] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.7 | 0 | AO3034 | Scheduling | C: For Sched
AI3037 | Selected Schedule Point [7] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.7 | 0 | AO3035 | Scheduling | C: For Sched
AI3038 | Selected Schedule Point [7] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.7 | 0 | AO3036 | Scheduling | C: For Sched
AI3039 | Selected Schedule Point [7] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.7 | 0 | AO3037 | Scheduling | C: For Sched
AI3040 | Selected Schedule Point [8] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.8 | 0 | AO3038 | Scheduling | C: For Sched
AI3041 | Selected Schedule Point [8] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.8 | 0 | AO3039 | Scheduling | C: For Sched
AI3042 | Selected Schedule Point [8] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.8 | 0 | AO3040 | Scheduling | C: For Sched
AI3043 | Selected Schedule Point [8] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.8 | 0 | AO3041 | Scheduling | C: For Sched
AI3044 | Selected Schedule Point [9] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.9 | 0 | AO3042 | Scheduling | C: For Sched
AI3045 | Selected Schedule Point [9] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.9 | 0 | AO3043 | Scheduling | C: For Sched
AI3046 | Selected Schedule Point [9] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.9 | 0 | AO3044 | Scheduling | C: For Sched
AI3047 | Selected Schedule Point [9] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.9 | 0 | AO3045 | Scheduling | C: For Sched
AI3048 | Selected Schedule Point [10] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.10 | 0 | AO3046 | Scheduling | C: For Sched
AI3049 | Selected Schedule Point [10] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.10 | 0 | AO3047 | Scheduling | C: For Sched
AI3050 | Selected Schedule Point [10] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.10 | 0 | AO3048 | Scheduling | C: For Sched
AI3051 | Selected Schedule Point [10] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.10 | 0 | AO3049 | Scheduling | C: For Sched
AI3052 | Selected Schedule Point [11] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.11 | 0 | AO3050 | Scheduling | C: For Sched
AI3053 | Selected Schedule Point [11] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.11 | 0 | AO3051 | Scheduling | C: For Sched
AI3054 | Selected Schedule Point [11] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.11 | 0 | AO3052 | Scheduling | C: For Sched
AI3055 | Selected Schedule Point [11] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.11 | 0 | AO3053 | Scheduling | C: For Sched
AI3056 | Selected Schedule Point [12] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.12 | 0 | AO3054 | Scheduling | C: For Sched
AI3057 | Selected Schedule Point [12] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.12 | 0 | AO3055 | Scheduling | C: For Sched
AI3058 | Selected Schedule Point [12] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.12 | 0 | AO3056 | Scheduling | C: For Sched
AI3059 | Selected Schedule Point [12] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.12 | 0 | AO3057 | Scheduling | C: For Sched
AI3060 | Selected Schedule Point [13] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.13 | 0 | AO3058 | Scheduling | C: For Sched
AI3061 | Selected Schedule Point [13] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.13 | 0 | AO3059 | Scheduling | C: For Sched
AI3062 | Selected Schedule Point [13] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.13 | 0 | AO3060 | Scheduling | C: For Sched
AI3063 | Selected Schedule Point [13] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.13 | 0 | AO3061 | Scheduling | C: For Sched
AI3064 | Selected Schedule Point [14] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.14 | 0 | AO3062 | Scheduling | C: For Sched
AI3065 | Selected Schedule Point [14] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.14 | 0 | AO3063 | Scheduling | C: For Sched
AI3066 | Selected Schedule Point [14] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.14 | 0 | AO3064 | Scheduling | C: For Sched
AI3067 | Selected Schedule Point [14] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.14 | 0 | AO3065 | Scheduling | C: For Sched
AI3068 | Selected Schedule Point [15] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.15 | 0 | AO3066 | Scheduling | C: For Sched
AI3069 | Selected Schedule Point [15] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.15 | 0 | AO3067 | Scheduling | C: For Sched
AI3070 | Selected Schedule Point [15] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.15 | 0 | AO3068 | Scheduling | C: For Sched
AI3071 | Selected Schedule Point [15] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.15 | 0 | AO3069 | Scheduling | C: For Sched
AI3072 | Selected Schedule Point [16] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.16 | 0 | AO3070 | Scheduling | C: For Sched
AI3073 | Selected Schedule Point [16] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.16 | 0 | AO3071 | Scheduling | C: For Sched
AI3074 | Selected Schedule Point [16] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.16 | 0 | AO3072 | Scheduling | C: For Sched
AI3075 | Selected Schedule Point [16] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.16 | 0 | AO3073 | Scheduling | C: For Sched
AI3076 | Selected Schedule Point [17] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.17 | 0 | AO3074 | Scheduling | C: For Sched
AI3077 | Selected Schedule Point [17] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.17 | 0 | AO3075 | Scheduling | C: For Sched
AI3078 | Selected Schedule Point [17] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.17 | 0 | AO3076 | Scheduling | C: For Sched
AI3079 | Selected Schedule Point [17] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.17 | 0 | AO3077 | Scheduling | C: For Sched
AI3080 | Selected Schedule Point [18] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.18 | 0 | AO3078 | Scheduling | C: For Sched
AI3081 | Selected Schedule Point [18] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.18 | 0 | AO3079 | Scheduling | C: For Sched
AI3082 | Selected Schedule Point [18] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.18 | 0 | AO3080 | Scheduling | C: For Sched
AI3083 | Selected Schedule Point [18] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.18 | 0 | AO3081 | Scheduling | C: For Sched
AI3084 | Selected Schedule Point [19] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.19 | 0 | AO3082 | Scheduling | C: For Sched
AI3085 | Selected Schedule Point [19] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.19 | 0 | AO3083 | Scheduling | C: For Sched
AI3086 | Selected Schedule Point [19] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.19 | 0 | AO3084 | Scheduling | C: For Sched
AI3087 | Selected Schedule Point [19] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.19 | 0 | AO3085 | Scheduling | C: For Sched
AI3088 | Selected Schedule Point [20] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.20 | 0 | AO3086 | Scheduling | C: For Sched
AI3089 | Selected Schedule Point [20] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.20 | 0 | AO3087 | Scheduling | C: For Sched
AI3090 | Selected Schedule Point [20] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.20 | 0 | AO3088 | Scheduling | C: For Sched
AI3091 | Selected Schedule Point [20] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.20 | 0 | AO3089 | Scheduling | C: For Sched
AI3092 | Selected Schedule Point [21] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.21 | 0 | AO3090 | Scheduling
AI3093 | Selected Schedule Point [21] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.21 | 0 | AO3091 | Scheduling
AI3094 | Selected Schedule Point [21] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.21 | 0 | AO3092 | Scheduling
AI3095 | Selected Schedule Point [21] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.21 | 0 | AO3093 | Scheduling
AI3096 | Selected Schedule Point [22] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.22 | 0 | AO3094 | Scheduling
AI3097 | Selected Schedule Point [22] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.22 | 0 | AO3095 | Scheduling
AI3098 | Selected Schedule Point [22] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.22 | 0 | AO3096 | Scheduling
AI3099 | Selected Schedule Point [22] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.22 | 0 | AO3097 | Scheduling
AI3100 | Selected Schedule Point [23] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.23 | 0 | AO3098 | Scheduling
AI3101 | Selected Schedule Point [23] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.23 | 0 | AO3099 | Scheduling
AI3102 | Selected Schedule Point [23] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.23 | 0 | AO3100 | Scheduling
AI3103 | Selected Schedule Point [23] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.23 | 0 | AO3101 | Scheduling
AI3104 | Selected Schedule Point [24] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.24 | 0 | AO3102 | Scheduling
AI3105 | Selected Schedule Point [24] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.24 | 0 | AO3103 | Scheduling
AI3106 | Selected Schedule Point [24] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.24 | 0 | AO3104 | Scheduling
AI3107 | Selected Schedule Point [24] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.24 | 0 | AO3105 | Scheduling
AI3108 | Selected Schedule Point [25] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.25 | 0 | AO3106 | Scheduling
AI3109 | Selected Schedule Point [25] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.25 | 0 | AO3107 | Scheduling
AI3110 | Selected Schedule Point [25] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.25 | 0 | AO3108 | Scheduling
AI3111 | Selected Schedule Point [25] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.25 | 0 | AO3109 | Scheduling
AI3112 | Selected Schedule Point [26] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.26 | 0 | AO3110 | Scheduling
AI3113 | Selected Schedule Point [26] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.26 | 0 | AO3111 | Scheduling
AI3114 | Selected Schedule Point [26] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.26 | 0 | AO3112 | Scheduling
AI3115 | Selected Schedule Point [26] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.26 | 0 | AO3113 | Scheduling
AI3116 | Selected Schedule Point [27] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.27 | 0 | AO3114 | Scheduling
AI3117 | Selected Schedule Point [27] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.27 | 0 | AO3115 | Scheduling
AI3118 | Selected Schedule Point [27] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.27 | 0 | AO3116 | Scheduling
AI3119 | Selected Schedule Point [27] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.27 | 0 | AO3117 | Scheduling
AI3120 | Selected Schedule Point [28] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.28 | 0 | AO3118 | Scheduling
AI3121 | Selected Schedule Point [28] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.28 | 0 | AO3119 | Scheduling
AI3122 | Selected Schedule Point [28] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.28 | 0 | AO3120 | Scheduling
AI3123 | Selected Schedule Point [28] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.28 | 0 | AO3121 | Scheduling
AI3124 | Selected Schedule Point [29] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.29 | 0 | AO3122 | Scheduling
AI3125 | Selected Schedule Point [29] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.29 | 0 | AO3123 | Scheduling
AI3126 | Selected Schedule Point [29] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.29 | 0 | AO3124 | Scheduling
AI3127 | Selected Schedule Point [29] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.29 | 0 | AO3125 | Scheduling
AI3128 | Selected Schedule Point [30] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.30 | 0 | AO3126 | Scheduling
AI3129 | Selected Schedule Point [30] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.30 | 0 | AO3127 | Scheduling
AI3130 | Selected Schedule Point [30] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.30 | 0 | AO3128 | Scheduling
AI3131 | Selected Schedule Point [30] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.30 | 0 | AO3129 | Scheduling
AI3132 | Selected Schedule Point [31] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.31 | 0 | AO3130 | Scheduling
AI3133 | Selected Schedule Point [31] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.31 | 0 | AO3131 | Scheduling
AI3134 | Selected Schedule Point [31] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.31 | 0 | AO3132 | Scheduling
AI3135 | Selected Schedule Point [31] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.31 | 0 | AO3133 | Scheduling
AI3136 | Selected Schedule Point [32] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.32 | 0 | AO3134 | Scheduling
AI3137 | Selected Schedule Point [32] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.32 | 0 | AO3135 | Scheduling
AI3138 | Selected Schedule Point [32] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.32 | 0 | AO3136 | Scheduling
AI3139 | Selected Schedule Point [32] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.32 | 0 | AO3137 | Scheduling
AI3140 | Selected Schedule Point [33] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.33 | 0 | AO3138 | Scheduling
AI3141 | Selected Schedule Point [33] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.33 | 0 | AO3139 | Scheduling
AI3142 | Selected Schedule Point [33] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.33 | 0 | AO3140 | Scheduling
AI3143 | Selected Schedule Point [33] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.33 | 0 | AO3141 | Scheduling
AI3144 | Selected Schedule Point [34] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.34 | 0 | AO3142 | Scheduling
AI3145 | Selected Schedule Point [34] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.34 | 0 | AO3143 | Scheduling
AI3146 | Selected Schedule Point [34] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.34 | 0 | AO3144 | Scheduling
AI3147 | Selected Schedule Point [34] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.34 | 0 | AO3145 | Scheduling
AI3148 | Selected Schedule Point [35] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.35 | 0 | AO3146 | Scheduling
AI3149 | Selected Schedule Point [35] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.35 | 0 | AO3147 | Scheduling
AI3150 | Selected Schedule Point [35] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.35 | 0 | AO3148 | Scheduling
AI3151 | Selected Schedule Point [35] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.35 | 0 | AO3149 | Scheduling
AI3152 | Selected Schedule Point [36] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.36 | 0 | AO3150 | Scheduling
AI3153 | Selected Schedule Point [36] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.36 | 0 | AO3151 | Scheduling
AI3154 | Selected Schedule Point [36] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.36 | 0 | AO3152 | Scheduling
AI3155 | Selected Schedule Point [36] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.36 | 0 | AO3153 | Scheduling
AI3156 | Selected Schedule Point [37] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.37 | 0 | AO3154 | Scheduling
AI3157 | Selected Schedule Point [37] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.37 | 0 | AO3155 | Scheduling
AI3158 | Selected Schedule Point [37] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.37 | 0 | AO3156 | Scheduling
AI3159 | Selected Schedule Point [37] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.37 | 0 | AO3157 | Scheduling
AI3160 | Selected Schedule Point [38] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.38 | 0 | AO3158 | Scheduling
AI3161 | Selected Schedule Point [38] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.38 | 0 | AO3159 | Scheduling
AI3162 | Selected Schedule Point [38] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.38 | 0 | AO3160 | Scheduling
AI3163 | Selected Schedule Point [38] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.38 | 0 | AO3161 | Scheduling
AI3164 | Selected Schedule Point [39] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.39 | 0 | AO3162 | Scheduling
AI3165 | Selected Schedule Point [39] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.39 | 0 | AO3163 | Scheduling
AI3166 | Selected Schedule Point [39] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.39 | 0 | AO3164 | Scheduling
AI3167 | Selected Schedule Point [39] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.39 | 0 | AO3165 | Scheduling
AI3168 | Selected Schedule Point [40] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.40 | 0 | AO3166 | Scheduling
AI3169 | Selected Schedule Point [40] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.40 | 0 | AO3167 | Scheduling
AI3170 | Selected Schedule Point [40] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.40 | 0 | AO3168 | Scheduling
AI3171 | Selected Schedule Point [40] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.40 | 0 | AO3169 | Scheduling
AI3172 | Selected Schedule Point [41] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.41 | 0 | AO3170 | Scheduling
AI3173 | Selected Schedule Point [41] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.41 | 0 | AO3171 | Scheduling
AI3174 | Selected Schedule Point [41] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.41 | 0 | AO3172 | Scheduling
AI3175 | Selected Schedule Point [41] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.41 | 0 | AO3173 | Scheduling
AI3176 | Selected Schedule Point [42] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.42 | 0 | AO3174 | Scheduling
AI3177 | Selected Schedule Point [42] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.42 | 0 | AO3175 | Scheduling
AI3178 | Selected Schedule Point [42] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.42 | 0 | AO3176 | Scheduling
AI3179 | Selected Schedule Point [42] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.42 | 0 | AO3177 | Scheduling
AI3180 | Selected Schedule Point [43] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.43 | 0 | AO3178 | Scheduling
AI3181 | Selected Schedule Point [43] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.43 | 0 | AO3179 | Scheduling
AI3182 | Selected Schedule Point [43] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.43 | 0 | AO3180 | Scheduling
AI3183 | Selected Schedule Point [43] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.43 | 0 | AO3181 | Scheduling
AI3184 | Selected Schedule Point [44] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.44 | 0 | AO3182 | Scheduling
AI3185 | Selected Schedule Point [44] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.44 | 0 | AO3183 | Scheduling
AI3186 | Selected Schedule Point [44] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.44 | 0 | AO3184 | Scheduling
AI3187 | Selected Schedule Point [44] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.44 | 0 | AO3185 | Scheduling
AI3188 | Selected Schedule Point [45] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.45 | 0 | AO3186 | Scheduling
AI3189 | Selected Schedule Point [45] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.45 | 0 | AO3187 | Scheduling
AI3190 | Selected Schedule Point [45] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.45 | 0 | AO3188 | Scheduling
AI3191 | Selected Schedule Point [45] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.45 | 0 | AO3189 | Scheduling
AI3192 | Selected Schedule Point [46] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.46 | 0 | AO3190 | Scheduling
AI3193 | Selected Schedule Point [46] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.46 | 0 | AO3191 | Scheduling
AI3194 | Selected Schedule Point [46] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.46 | 0 | AO3192 | Scheduling
AI3195 | Selected Schedule Point [46] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.46 | 0 | AO3193 | Scheduling
AI3196 | Selected Schedule Point [47] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.47 | 0 | AO3194 | Scheduling
AI3197 | Selected Schedule Point [47] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.47 | 0 | AO3195 | Scheduling
AI3198 | Selected Schedule Point [47] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.47 | 0 | AO3196 | Scheduling
AI3199 | Selected Schedule Point [47] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.47 | 0 | AO3197 | Scheduling
AI3200 | Selected Schedule Point [48] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.48 | 0 | AO3198 | Scheduling
AI3201 | Selected Schedule Point [48] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.48 | 0 | AO3199 | Scheduling
AI3202 | Selected Schedule Point [48] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.48 | 0 | AO3200 | Scheduling
AI3203 | Selected Schedule Point [48] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.48 | 0 | AO3201 | Scheduling
AI3204 | Selected Schedule Point [49] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.49 | 0 | AO3202 | Scheduling
AI3205 | Selected Schedule Point [49] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.49 | 0 | AO3203 | Scheduling
AI3206 | Selected Schedule Point [49] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.49 | 0 | AO3204 | Scheduling
AI3207 | Selected Schedule Point [49] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.49 | 0 | AO3205 | Scheduling
AI3208 | Selected Schedule Point [50] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.50 | 0 | AO3206 | Scheduling
AI3209 | Selected Schedule Point [50] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.50 | 0 | AO3207 | Scheduling
AI3210 | Selected Schedule Point [50] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.50 | 0 | AO3208 | Scheduling
AI3211 | Selected Schedule Point [50] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.50 | 0 | AO3209 | Scheduling
AI3212 | Selected Schedule Point [51] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.51 | 0 | AO3210 | Scheduling
AI3213 | Selected Schedule Point [51] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.51 | 0 | AO3211 | Scheduling
AI3214 | Selected Schedule Point [51] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.51 | 0 | AO3212 | Scheduling
AI3215 | Selected Schedule Point [51] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.51 | 0 | AO3213 | Scheduling
AI3216 | Selected Schedule Point [52] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.52 | 0 | AO3214 | Scheduling
AI3217 | Selected Schedule Point [52] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.52 | 0 | AO3215 | Scheduling
AI3218 | Selected Schedule Point [52] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.52 | 0 | AO3216 | Scheduling
AI3219 | Selected Schedule Point [52] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.52 | 0 | AO3217 | Scheduling
AI3220 | Selected Schedule Point [53] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.53 | 0 | AO3218 | Scheduling
AI3221 | Selected Schedule Point [53] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.53 | 0 | AO3219 | Scheduling
AI3222 | Selected Schedule Point [53] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.53 | 0 | AO3220 | Scheduling
AI3223 | Selected Schedule Point [53] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.53 | 0 | AO3221 | Scheduling
AI3224 | Selected Schedule Point [54] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.54 | 0 | AO3222 | Scheduling
AI3225 | Selected Schedule Point [54] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.54 | 0 | AO3223 | Scheduling
AI3226 | Selected Schedule Point [54] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.54 | 0 | AO3224 | Scheduling
AI3227 | Selected Schedule Point [54] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.54 | 0 | AO3225 | Scheduling
AI3228 | Selected Schedule Point [55] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.55 | 0 | AO3226 | Scheduling
AI3229 | Selected Schedule Point [55] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.55 | 0 | AO3227 | Scheduling
AI3230 | Selected Schedule Point [55] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.55 | 0 | AO3228 | Scheduling
AI3231 | Selected Schedule Point [55] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.55 | 0 | AO3229 | Scheduling
AI3232 | Selected Schedule Point [56] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.56 | 0 | AO3230 | Scheduling
AI3233 | Selected Schedule Point [56] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.56 | 0 | AO3231 | Scheduling
AI3234 | Selected Schedule Point [56] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.56 | 0 | AO3232 | Scheduling
AI3235 | Selected Schedule Point [56] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.56 | 0 | AO3233 | Scheduling
AI3236 | Selected Schedule Point [57] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.57 | 0 | AO3234 | Scheduling
AI3237 | Selected Schedule Point [57] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.57 | 0 | AO3235 | Scheduling
AI3238 | Selected Schedule Point [57] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.57 | 0 | AO3236 | Scheduling
AI3239 | Selected Schedule Point [57] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.57 | 0 | AO3237 | Scheduling
AI3240 | Selected Schedule Point [58] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.58 | 0 | AO3238 | Scheduling
AI3241 | Selected Schedule Point [58] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.58 | 0 | AO3239 | Scheduling
AI3242 | Selected Schedule Point [58] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.58 | 0 | AO3240 | Scheduling
AI3243 | Selected Schedule Point [58] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.58 | 0 | AO3241 | Scheduling
AI3244 | Selected Schedule Point [59] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.59 | 0 | AO3242 | Scheduling
AI3245 | Selected Schedule Point [59] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.59 | 0 | AO3243 | Scheduling
AI3246 | Selected Schedule Point [59] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.59 | 0 | AO3244 | Scheduling
AI3247 | Selected Schedule Point [59] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.59 | 0 | AO3245 | Scheduling
AI3248 | Selected Schedule Point [60] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.60 | 0 | AO3246 | Scheduling
AI3249 | Selected Schedule Point [60] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.60 | 0 | AO3247 | Scheduling
AI3250 | Selected Schedule Point [60] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.60 | 0 | AO3248 | Scheduling
AI3251 | Selected Schedule Point [60] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.60 | 0 | AO3249 | Scheduling
AI3252 | Selected Schedule Point [61] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.61 | 0 | AO3250 | Scheduling
AI3253 | Selected Schedule Point [61] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.61 | 0 | AO3251 | Scheduling
AI3254 | Selected Schedule Point [61] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.61 | 0 | AO3252 | Scheduling
AI3255 | Selected Schedule Point [61] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.61 | 0 | AO3253 | Scheduling
AI3256 | Selected Schedule Point [62] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.62 | 0 | AO3254 | Scheduling
AI3257 | Selected Schedule Point [62] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.62 | 0 | AO3255 | Scheduling
AI3258 | Selected Schedule Point [62] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.62 | 0 | AO3256 | Scheduling
AI3259 | Selected Schedule Point [62] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.62 | 0 | AO3257 | Scheduling
AI3260 | Selected Schedule Point [63] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.63 | 0 | AO3258 | Scheduling
AI3261 | Selected Schedule Point [63] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.63 | 0 | AO3259 | Scheduling
AI3262 | Selected Schedule Point [63] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.63 | 0 | AO3260 | Scheduling
AI3263 | Selected Schedule Point [63] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.63 | 0 | AO3261 | Scheduling
AI3264 | Selected Schedule Point [64] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.64 | 0 | AO3262 | Scheduling
AI3265 | Selected Schedule Point [64] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.64 | 0 | AO3263 | Scheduling
AI3266 | Selected Schedule Point [64] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.64 | 0 | AO3264 | Scheduling
AI3267 | Selected Schedule Point [64] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.64 | 0 | AO3265 | Scheduling
AI3268 | Selected Schedule Point [65] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.65 | 0 | AO3266 | Scheduling
AI3269 | Selected Schedule Point [65] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.65 | 0 | AO3267 | Scheduling
AI3270 | Selected Schedule Point [65] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.65 | 0 | AO3268 | Scheduling
AI3271 | Selected Schedule Point [65] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.65 | 0 | AO3269 | Scheduling
AI3272 | Selected Schedule Point [66] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.66 | 0 | AO3270 | Scheduling
AI3273 | Selected Schedule Point [66] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.66 | 0 | AO3271 | Scheduling
AI3274 | Selected Schedule Point [66] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.66 | 0 | AO3272 | Scheduling
AI3275 | Selected Schedule Point [66] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.66 | 0 | AO3273 | Scheduling
AI3276 | Selected Schedule Point [67] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.67 | 0 | AO3274 | Scheduling
AI3277 | Selected Schedule Point [67] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.67 | 0 | AO3275 | Scheduling
AI3278 | Selected Schedule Point [67] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.67 | 0 | AO3276 | Scheduling
AI3279 | Selected Schedule Point [67] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.67 | 0 | AO3277 | Scheduling
AI3280 | Selected Schedule Point [68] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.68 | 0 | AO3278 | Scheduling
AI3281 | Selected Schedule Point [68] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.68 | 0 | AO3279 | Scheduling
AI3282 | Selected Schedule Point [68] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.68 | 0 | AO3280 | Scheduling
AI3283 | Selected Schedule Point [68] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.68 | 0 | AO3281 | Scheduling
AI3284 | Selected Schedule Point [69] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.69 | 0 | AO3282 | Scheduling
AI3285 | Selected Schedule Point [69] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.69 | 0 | AO3283 | Scheduling
AI3286 | Selected Schedule Point [69] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.69 | 0 | AO3284 | Scheduling
AI3287 | Selected Schedule Point [69] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.69 | 0 | AO3285 | Scheduling
AI3288 | Selected Schedule Point [70] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.70 | 0 | AO3286 | Scheduling
AI3289 | Selected Schedule Point [70] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.70 | 0 | AO3287 | Scheduling
AI3290 | Selected Schedule Point [70] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.70 | 0 | AO3288 | Scheduling
AI3291 | Selected Schedule Point [70] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.70 | 0 | AO3289 | Scheduling
AI3292 | Selected Schedule Point [71] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.71 | 0 | AO3290 | Scheduling
AI3293 | Selected Schedule Point [71] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.71 | 0 | AO3291 | Scheduling
AI3294 | Selected Schedule Point [71] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.71 | 0 | AO3292 | Scheduling
AI3295 | Selected Schedule Point [71] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.71 | 0 | AO3293 | Scheduling
AI3296 | Selected Schedule Point [72] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.72 | 0 | AO3294 | Scheduling
AI3297 | Selected Schedule Point [72] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.72 | 0 | AO3295 | Scheduling
AI3298 | Selected Schedule Point [72] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.72 | 0 | AO3296 | Scheduling
AI3299 | Selected Schedule Point [72] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.72 | 0 | AO3297 | Scheduling
AI3300 | Selected Schedule Point [73] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.73 | 0 | AO3298 | Scheduling
AI3301 | Selected Schedule Point [73] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.73 | 0 | AO3299 | Scheduling
AI3302 | Selected Schedule Point [73] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.73 | 0 | AO3300 | Scheduling
AI3303 | Selected Schedule Point [73] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.73 | 0 | AO3301 | Scheduling
AI3304 | Selected Schedule Point [74] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.74 | 0 | AO3302 | Scheduling
AI3305 | Selected Schedule Point [74] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.74 | 0 | AO3303 | Scheduling
AI3306 | Selected Schedule Point [74] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.74 | 0 | AO3304 | Scheduling
AI3307 | Selected Schedule Point [74] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.74 | 0 | AO3305 | Scheduling
AI3308 | Selected Schedule Point [75] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.75 | 0 | AO3306 | Scheduling
AI3309 | Selected Schedule Point [75] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.75 | 0 | AO3307 | Scheduling
AI3310 | Selected Schedule Point [75] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.75 | 0 | AO3308 | Scheduling
AI3311 | Selected Schedule Point [75] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.75 | 0 | AO3309 | Scheduling
AI3312 | Selected Schedule Point [76] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.76 | 0 | AO3310 | Scheduling
AI3313 | Selected Schedule Point [76] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.76 | 0 | AO3311 | Scheduling
AI3314 | Selected Schedule Point [76] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.76 | 0 | AO3312 | Scheduling
AI3315 | Selected Schedule Point [76] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.76 | 0 | AO3313 | Scheduling
AI3316 | Selected Schedule Point [77] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.77 | 0 | AO3314 | Scheduling
AI3317 | Selected Schedule Point [77] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.77 | 0 | AO3315 | Scheduling
AI3318 | Selected Schedule Point [77] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.77 | 0 | AO3316 | Scheduling
AI3319 | Selected Schedule Point [77] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.77 | 0 | AO3317 | Scheduling
AI3320 | Selected Schedule Point [78] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.78 | 0 | AO3318 | Scheduling
AI3321 | Selected Schedule Point [78] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.78 | 0 | AO3319 | Scheduling
AI3322 | Selected Schedule Point [78] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.78 | 0 | AO3320 | Scheduling
AI3323 | Selected Schedule Point [78] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.78 | 0 | AO3321 | Scheduling
AI3324 | Selected Schedule Point [79] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.79 | 0 | AO3322 | Scheduling
AI3325 | Selected Schedule Point [79] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.79 | 0 | AO3323 | Scheduling
AI3326 | Selected Schedule Point [79] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.79 | 0 | AO3324 | Scheduling
AI3327 | Selected Schedule Point [79] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.79 | 0 | AO3325 | Scheduling
AI3328 | Selected Schedule Point [80] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.80 | 0 | AO3326 | Scheduling
AI3329 | Selected Schedule Point [80] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.80 | 0 | AO3327 | Scheduling
AI3330 | Selected Schedule Point [80] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.80 | 0 | AO3328 | Scheduling
AI3331 | Selected Schedule Point [80] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.80 | 0 | AO3329 | Scheduling
AI3332 | Selected Schedule Point [81] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.81 | 0 | AO3330 | Scheduling
AI3333 | Selected Schedule Point [81] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.81 | 0 | AO3331 | Scheduling
AI3334 | Selected Schedule Point [81] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.81 | 0 | AO3332 | Scheduling
AI3335 | Selected Schedule Point [81] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.81 | 0 | AO3333 | Scheduling
AI3336 | Selected Schedule Point [82] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.82 | 0 | AO3334 | Scheduling
AI3337 | Selected Schedule Point [82] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.82 | 0 | AO3335 | Scheduling
AI3338 | Selected Schedule Point [82] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.82 | 0 | AO3336 | Scheduling
AI3339 | Selected Schedule Point [82] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.82 | 0 | AO3337 | Scheduling
AI3340 | Selected Schedule Point [83] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.83 | 0 | AO3338 | Scheduling
AI3341 | Selected Schedule Point [83] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.83 | 0 | AO3339 | Scheduling
AI3342 | Selected Schedule Point [83] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.83 | 0 | AO3340 | Scheduling
AI3343 | Selected Schedule Point [83] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.83 | 0 | AO3341 | Scheduling
AI3344 | Selected Schedule Point [84] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.84 | 0 | AO3342 | Scheduling
AI3345 | Selected Schedule Point [84] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.84 | 0 | AO3343 | Scheduling
AI3346 | Selected Schedule Point [84] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.84 | 0 | AO3344 | Scheduling
AI3347 | Selected Schedule Point [84] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.84 | 0 | AO3345 | Scheduling
AI3348 | Selected Schedule Point [85] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.85 | 0 | AO3346 | Scheduling
AI3349 | Selected Schedule Point [85] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.85 | 0 | AO3347 | Scheduling
AI3350 | Selected Schedule Point [85] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.85 | 0 | AO3348 | Scheduling
AI3351 | Selected Schedule Point [85] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.85 | 0 | AO3349 | Scheduling
AI3352 | Selected Schedule Point [86] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.86 | 0 | AO3350 | Scheduling
AI3353 | Selected Schedule Point [86] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.86 | 0 | AO3351 | Scheduling
AI3354 | Selected Schedule Point [86] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.86 | 0 | AO3352 | Scheduling
AI3355 | Selected Schedule Point [86] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.86 | 0 | AO3353 | Scheduling
AI3356 | Selected Schedule Point [87] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.87 | 0 | AO3354 | Scheduling
AI3357 | Selected Schedule Point [87] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.87 | 0 | AO3355 | Scheduling
AI3358 | Selected Schedule Point [87] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.87 | 0 | AO3356 | Scheduling
AI3359 | Selected Schedule Point [87] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.87 | 0 | AO3357 | Scheduling
AI3360 | Selected Schedule Point [88] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.88 | 0 | AO3358 | Scheduling
AI3361 | Selected Schedule Point [88] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.88 | 0 | AO3359 | Scheduling
AI3362 | Selected Schedule Point [88] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.88 | 0 | AO3360 | Scheduling
AI3363 | Selected Schedule Point [88] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.88 | 0 | AO3361 | Scheduling
AI3364 | Selected Schedule Point [89] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.89 | 0 | AO3362 | Scheduling
AI3365 | Selected Schedule Point [89] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.89 | 0 | AO3363 | Scheduling
AI3366 | Selected Schedule Point [89] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.89 | 0 | AO3364 | Scheduling
AI3367 | Selected Schedule Point [89] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.89 | 0 | AO3365 | Scheduling
AI3368 | Selected Schedule Point [90] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.90 | 0 | AO3366 | Scheduling
AI3369 | Selected Schedule Point [90] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.90 | 0 | AO3367 | Scheduling
AI3370 | Selected Schedule Point [90] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.90 | 0 | AO3368 | Scheduling
AI3371 | Selected Schedule Point [90] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.90 | 0 | AO3369 | Scheduling
AI3372 | Selected Schedule Point [91] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.91 | 0 | AO3370 | Scheduling
AI3373 | Selected Schedule Point [91] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.91 | 0 | AO3371 | Scheduling
AI3374 | Selected Schedule Point [91] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.91 | 0 | AO3372 | Scheduling
AI3375 | Selected Schedule Point [91] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.91 | 0 | AO3373 | Scheduling
AI3376 | Selected Schedule Point [92] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.92 | 0 | AO3374 | Scheduling
AI3377 | Selected Schedule Point [92] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.92 | 0 | AO3375 | Scheduling
AI3378 | Selected Schedule Point [92] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.92 | 0 | AO3376 | Scheduling
AI3379 | Selected Schedule Point [92] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.92 | 0 | AO3377 | Scheduling
AI3380 | Selected Schedule Point [93] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.93 | 0 | AO3378 | Scheduling
AI3381 | Selected Schedule Point [93] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.93 | 0 | AO3379 | Scheduling
AI3382 | Selected Schedule Point [93] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.93 | 0 | AO3380 | Scheduling
AI3383 | Selected Schedule Point [93] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.93 | 0 | AO3381 | Scheduling
AI3384 | Selected Schedule Point [94] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.94 | 0 | AO3382 | Scheduling
AI3385 | Selected Schedule Point [94] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.94 | 0 | AO3383 | Scheduling
AI3386 | Selected Schedule Point [94] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.94 | 0 | AO3384 | Scheduling
AI3387 | Selected Schedule Point [94] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.94 | 0 | AO3385 | Scheduling
AI3388 | Selected Schedule Point [95] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.95 | 0 | AO3386 | Scheduling
AI3389 | Selected Schedule Point [95] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.95 | 0 | AO3387 | Scheduling
AI3390 | Selected Schedule Point [95] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.95 | 0 | AO3388 | Scheduling
AI3391 | Selected Schedule Point [95] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.95 | 0 | AO3389 | Scheduling
AI3392 | Selected Schedule Point [96] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.96 | 0 | AO3390 | Scheduling
AI3393 | Selected Schedule Point [96] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.96 | 0 | AO3391 | Scheduling
AI3394 | Selected Schedule Point [96] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.96 | 0 | AO3392 | Scheduling
AI3395 | Selected Schedule Point [96] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.96 | 0 | AO3393 | Scheduling
AI3396 | Selected Schedule Point [97] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.97 | 0 | AO3394 | Scheduling
AI3397 | Selected Schedule Point [97] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.97 | 0 | AO3395 | Scheduling
AI3398 | Selected Schedule Point [97] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.97 | 0 | AO3396 | Scheduling
AI3399 | Selected Schedule Point [97] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.97 | 0 | AO3397 | Scheduling
AI3400 | Selected Schedule Point [98] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.98 | 0 | AO3398 | Scheduling
AI3401 | Selected Schedule Point [98] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.98 | 0 | AO3399 | Scheduling
AI3402 | Selected Schedule Point [98] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.98 | 0 | AO3400 | Scheduling
AI3403 | Selected Schedule Point [98] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.98 | 0 | AO3401 | Scheduling
AI3404 | Selected Schedule Point [99] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.99 | 0 | AO3402 | Scheduling
AI3405 | Selected Schedule Point [99] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.99 | 0 | AO3403 | Scheduling
AI3406 | Selected Schedule Point [99] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.99 | 0 | AO3404 | Scheduling
AI3407 | Selected Schedule Point [99] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.99 | 0 | AO3405 | Scheduling
AI3408 | Selected Schedule Point [100] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.100 | 0 | AO3406 | Scheduling
AI3409 | Selected Schedule Point [100] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.100 | 0 | AO3407 | Scheduling
AI3410 | Selected Schedule Point [100] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.100 | 0 | AO3408 | Scheduling
AI3411 | Selected Schedule Point [100] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.100 | 0 | AO3409 | Scheduling
AI3500 | Schedule [1] Status Editing = 1; Submitted = 2; Validated = 3; Enabled = 4; Running = 5; Running but not Active = 6, Cycle Completed = 7; Completed and Expired = 8; Disabled = 9; Invalid = 10; Error = 11 | 2 | 0 | 11 | 1 | 0 | Enum | FSCH1.SchdSt | 0 |  | Scheduling | C: For Sched
AI3501 | Schedule [1] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH1.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3502 | Schedule [1] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH1.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3503 | Schedule [2] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH2.SchdSt | 0 |  | Scheduling | C: For Sched
AI3504 | Schedule [2] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH2.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3505 | Schedule [2] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH2.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3506 | Schedule [3] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH3.SchdSt | 0 |  | Scheduling | C: For Sched
AI3507 | Schedule [3] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH3.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3508 | Schedule [3] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH3.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3509 | Schedule [4] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH4.SchdSt | 0 |  | Scheduling | C: For Sched
AI3510 | Schedule [4] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH4.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3511 | Schedule [4] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH4.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3512 | Schedule [5] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH5.SchdSt | 0 |  | Scheduling | C: For Sched
AI3513 | Schedule [5] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH5.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3514 | Schedule [5] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH5.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3515 | Schedule [6] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH6.SchdSt | 0 |  | Scheduling | C: For Sched
AI3516 | Schedule [6] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH6.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3517 | Schedule [6] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH6.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3518 | Schedule [7] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH7.SchdSt | 0 |  | Scheduling | C: For Sched
AI3519 | Schedule [7] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH7.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3520 | Schedule [7] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH7.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3521 | Schedule [8] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH8.SchdSt | 0 |  | Scheduling | C: For Sched
AI3522 | Schedule [8] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH8.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3523 | Schedule [8] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH8.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3524 | Schedule [9] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH9.SchdSt | 0 |  | Scheduling | C: For Sched
AI3525 | Schedule [9] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH9.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3526 | Schedule [9] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH9.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3527 | Schedule [10] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH10.SchdSt | 0 |  | Scheduling | C: For Sched
AI3528 | Schedule [10] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH10.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3529 | Schedule [10] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH10.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3530 | Schedule [11] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH11.SchdSt | 0 |  | Scheduling | C: For Sched
AI3531 | Schedule [11] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH11.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3532 | Schedule [11] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH11.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3533 | Schedule [12] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH12.SchdSt | 0 |  | Scheduling | C: For Sched
AI3534 | Schedule [12] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH12.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3535 | Schedule [12] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH12.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3536 | Schedule [13] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH13.SchdSt | 0 |  | Scheduling | C: For Sched
AI3537 | Schedule [13] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH13.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3538 | Schedule [13] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH13.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3539 | Schedule [14] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH14.SchdSt | 0 |  | Scheduling | C: For Sched
AI3540 | Schedule [14] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH14.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3541 | Schedule [14] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH14.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3542 | Schedule [15] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH15.SchdSt | 0 |  | Scheduling | C: For Sched
AI3543 | Schedule [15] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH15.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3544 | Schedule [15] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH15.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3545 | Schedule [16] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH16.SchdSt | 0 |  | Scheduling | C: For Sched
AI3546 | Schedule [16] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH16.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3547 | Schedule [16] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH16.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3548 | Schedule [17] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH17.SchdSt | 0 |  | Scheduling | C: For Sched
AI3549 | Schedule [17] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH17.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3550 | Schedule [17] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH17.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3551 | Schedule [18] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH18.SchdSt | 0 |  | Scheduling | C: For Sched
AI3552 | Schedule [18] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH18.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3553 | Schedule [18] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH18.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3554 | Schedule [19] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH19.SchdSt | 0 |  | Scheduling | C: For Sched
AI3555 | Schedule [19] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH19.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3556 | Schedule [19] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH19.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3557 | Schedule [20] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH20.SchdSt | 0 |  | Scheduling | C: For Sched
AI3558 | Schedule [20] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH20.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3559 | Schedule [20] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH20.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3560 | Schedule [21] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH21.SchdSt | 0 |  | Scheduling
AI3561 | Schedule [21] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH21.SchdPrio | 1 |  | Scheduling
AI3562 | Schedule [21] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH21.ActStrTm | 0 |  | Scheduling
AI3563 | Schedule [22] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH22.SchdSt | 0 |  | Scheduling
AI3564 | Schedule [22] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH22.SchdPrio | 1 |  | Scheduling
AI3565 | Schedule [22] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH22.ActStrTm | 0 |  | Scheduling
AI3566 | Schedule [23] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH23.SchdSt | 0 |  | Scheduling
AI3567 | Schedule [23] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH23.SchdPrio | 1 |  | Scheduling
AI3568 | Schedule [23] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH23.ActStrTm | 0 |  | Scheduling
AI3569 | Schedule [24] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH24.SchdSt | 0 |  | Scheduling
AI3570 | Schedule [24] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH24.SchdPrio | 1 |  | Scheduling
AI3571 | Schedule [24] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH24.ActStrTm | 0 |  | Scheduling
AI3572 | Schedule [25] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH25.SchdSt | 0 |  | Scheduling
AI3573 | Schedule [25] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH25.SchdPrio | 1 |  | Scheduling
AI3574 | Schedule [25] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH25.ActStrTm | 0 |  | Scheduling
AI3575 | Schedule [26] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH26.SchdSt | 0 |  | Scheduling
AI3576 | Schedule [26] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH26.SchdPrio | 1 |  | Scheduling
AI3577 | Schedule [26] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH26.ActStrTm | 0 |  | Scheduling
AI3578 | Schedule [27] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH27.SchdSt | 0 |  | Scheduling
AI3579 | Schedule [27] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH27.SchdPrio | 1 |  | Scheduling
AI3580 | Schedule [27] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH27.ActStrTm | 0 |  | Scheduling
AI3581 | Schedule [28] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH28.SchdSt | 0 |  | Scheduling
AI3582 | Schedule [28] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH28.SchdPrio | 1 |  | Scheduling
AI3583 | Schedule [28] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH28.ActStrTm | 0 |  | Scheduling
AI3584 | Schedule [29] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH29.SchdSt | 0 |  | Scheduling
AI3585 | Schedule [29] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH29.SchdPrio | 1 |  | Scheduling
AI3586 | Schedule [29] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH29.ActStrTm | 0 |  | Scheduling
AI3587 | Schedule [30] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH30.SchdSt | 0 |  | Scheduling
AI3588 | Schedule [30] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH30.SchdPrio | 1 |  | Scheduling
AI3589 | Schedule [30] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH30.ActStrTm | 0 |  | Scheduling
AI3590 | Schedule [31] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH31.SchdSt | 0 |  | Scheduling
AI3591 | Schedule [31] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH31.SchdPrio | 1 |  | Scheduling
AI3592 | Schedule [31] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH31.ActStrTm | 0 |  | Scheduling
AI3593 | Schedule [32] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH32.SchdSt | 0 |  | Scheduling
AI3594 | Schedule [32] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH32.SchdPrio | 1 |  | Scheduling
AI3595 | Schedule [32] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH32.ActStrTm | 0 |  | Scheduling
AI3596 | Schedule [33] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH33.SchdSt | 0 |  | Scheduling
AI3597 | Schedule [33] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH33.SchdPrio | 1 |  | Scheduling
AI3598 | Schedule [33] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH33.ActStrTm | 0 |  | Scheduling
AI3599 | Schedule [34] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH34.SchdSt | 0 |  | Scheduling
AI3600 | Schedule [34] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH34.SchdPrio | 1 |  | Scheduling
AI3601 | Schedule [34] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH34.ActStrTm | 0 |  | Scheduling
AI3602 | Schedule [35] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH35.SchdSt | 0 |  | Scheduling
AI3603 | Schedule [35] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH35.SchdPrio | 1 |  | Scheduling
AI3604 | Schedule [35] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH35.ActStrTm | 0 |  | Scheduling
AI3605 | Schedule [36] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH36.SchdSt | 0 |  | Scheduling
AI3606 | Schedule [36] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH36.SchdPrio | 1 |  | Scheduling
AI3607 | Schedule [36] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH36.ActStrTm | 0 |  | Scheduling
AI3608 | Schedule [37] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH37.SchdSt | 0 |  | Scheduling
AI3609 | Schedule [37] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH37.SchdPrio | 1 |  | Scheduling
AI3610 | Schedule [37] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH37.ActStrTm | 0 |  | Scheduling
AI3611 | Schedule [38] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH38.SchdSt | 0 |  | Scheduling
AI3612 | Schedule [38] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH38.SchdPrio | 1 |  | Scheduling
AI3613 | Schedule [38] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH38.ActStrTm | 0 |  | Scheduling
AI3614 | Schedule [39] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH39.SchdSt | 0 |  | Scheduling
AI3615 | Schedule [39] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH39.SchdPrio | 1 |  | Scheduling
AI3616 | Schedule [39] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH39.ActStrTm | 0 |  | Scheduling
AI3617 | Schedule [40] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH40.SchdSt | 0 |  | Scheduling
AI3618 | Schedule [40] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH40.SchdPrio | 1 |  | Scheduling
AI3619 | Schedule [40] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH40.ActStrTm | 0 |  | Scheduling
AI3620 | Schedule [41] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH41.SchdSt | 0 |  | Scheduling
AI3621 | Schedule [41] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH41.SchdPrio | 1 |  | Scheduling
AI3622 | Schedule [41] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH41.ActStrTm | 0 |  | Scheduling
AI3623 | Schedule [42] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH42.SchdSt | 0 |  | Scheduling
AI3624 | Schedule [42] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH42.SchdPrio | 1 |  | Scheduling
AI3625 | Schedule [42] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH42.ActStrTm | 0 |  | Scheduling
AI3626 | Schedule [43] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH43.SchdSt | 0 |  | Scheduling
AI3627 | Schedule [43] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH43.SchdPrio | 1 |  | Scheduling
AI3628 | Schedule [43] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH43.ActStrTm | 0 |  | Scheduling
AI3629 | Schedule [44] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH44.SchdSt | 0 |  | Scheduling
AI3630 | Schedule [44] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH44.SchdPrio | 1 |  | Scheduling
AI3631 | Schedule [44] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH44.ActStrTm | 0 |  | Scheduling
AI3632 | Schedule [45] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH45.SchdSt | 0 |  | Scheduling
AI3633 | Schedule [45] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH45.SchdPrio | 1 |  | Scheduling
AI3634 | Schedule [45] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH45.ActStrTm | 0 |  | Scheduling
AI3635 | Schedule [46] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH46.SchdSt | 0 |  | Scheduling
AI3636 | Schedule [46] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH46.SchdPrio | 1 |  | Scheduling
AI3637 | Schedule [46] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH46.ActStrTm | 0 |  | Scheduling
AI3638 | Schedule [47] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH47.SchdSt | 0 |  | Scheduling
AI3639 | Schedule [47] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH47.SchdPrio | 1 |  | Scheduling
AI3640 | Schedule [47] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH47.ActStrTm | 0 |  | Scheduling
AI3641 | Schedule [48] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH48.SchdSt | 0 |  | Scheduling
AI3642 | Schedule [48] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH48.SchdPrio | 1 |  | Scheduling
AI3643 | Schedule [48] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH48.ActStrTm | 0 |  | Scheduling
AI3644 | Schedule [49] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH49.SchdSt | 0 |  | Scheduling
AI3645 | Schedule [49] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH49.SchdPrio | 1 |  | Scheduling
AI3646 | Schedule [49] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH49.ActStrTm | 0 |  | Scheduling
AI3647 | Schedule [50] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH50.SchdSt | 0 |  | Scheduling
AI3648 | Schedule [50] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH50.SchdPrio | 1 |  | Scheduling
AI3649 | Schedule [50] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH50.ActStrTm | 0 |  | Scheduling
AI3650 | Schedule [51] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH51.SchdSt | 0 |  | Scheduling
AI3651 | Schedule [51] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH51.SchdPrio | 1 |  | Scheduling
AI3652 | Schedule [51] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH51.ActStrTm | 0 |  | Scheduling
AI3653 | Schedule [52] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH52.SchdSt | 0 |  | Scheduling
AI3654 | Schedule [52] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH52.SchdPrio | 1 |  | Scheduling
AI3655 | Schedule [52] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH52.ActStrTm | 0 |  | Scheduling
AI3656 | Schedule [53] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH53.SchdSt | 0 |  | Scheduling
AI3657 | Schedule [53] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH53.SchdPrio | 1 |  | Scheduling
AI3658 | Schedule [53] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH53.ActStrTm | 0 |  | Scheduling
AI3659 | Schedule [54] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH54.SchdSt | 0 |  | Scheduling
AI3660 | Schedule [54] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH54.SchdPrio | 1 |  | Scheduling
AI3661 | Schedule [54] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH54.ActStrTm | 0 |  | Scheduling
AI3662 | Schedule [55] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH55.SchdSt | 0 |  | Scheduling
AI3663 | Schedule [55] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH55.SchdPrio | 1 |  | Scheduling
AI3664 | Schedule [55] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH55.ActStrTm | 0 |  | Scheduling
AI3665 | Schedule [56] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH56.SchdSt | 0 |  | Scheduling
AI3666 | Schedule [56] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH56.SchdPrio | 1 |  | Scheduling
AI3667 | Schedule [56] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH56.ActStrTm | 0 |  | Scheduling
AI3668 | Schedule [57] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH57.SchdSt | 0 |  | Scheduling
AI3669 | Schedule [57] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH57.SchdPrio | 1 |  | Scheduling
AI3670 | Schedule [57] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH57.ActStrTm | 0 |  | Scheduling
AI3671 | Schedule [58] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH58.SchdSt | 0 |  | Scheduling
AI3672 | Schedule [58] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH58.SchdPrio | 1 |  | Scheduling
AI3673 | Schedule [58] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH58.ActStrTm | 0 |  | Scheduling
AI3674 | Schedule [59] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH59.SchdSt | 0 |  | Scheduling
AI3675 | Schedule [59] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH59.SchdPrio | 1 |  | Scheduling
AI3676 | Schedule [59] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH59.ActStrTm | 0 |  | Scheduling
AI3677 | Schedule [60] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH60.SchdSt | 0 |  | Scheduling
AI3678 | Schedule [60] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH60.SchdPrio | 1 |  | Scheduling
AI3679 | Schedule [60] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH60.ActStrTm | 0 |  | Scheduling
AI3680 | Schedule [61] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH61.SchdSt | 0 |  | Scheduling
AI3681 | Schedule [61] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH61.SchdPrio | 1 |  | Scheduling
AI3682 | Schedule [61] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH61.ActStrTm | 0 |  | Scheduling
AI3683 | Schedule [62] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH62.SchdSt | 0 |  | Scheduling
AI3684 | Schedule [62] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH62.SchdPrio | 1 |  | Scheduling
AI3685 | Schedule [62] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH62.ActStrTm | 0 |  | Scheduling
AI3686 | Schedule [63] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH63.SchdSt | 0 |  | Scheduling
AI3687 | Schedule [63] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH63.SchdPrio | 1 |  | Scheduling
AI3688 | Schedule [63] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH63.ActStrTm | 0 |  | Scheduling
AI3689 | Schedule [64] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH64.SchdSt | 0 |  | Scheduling
AI3690 | Schedule [64] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH64.SchdPrio | 1 |  | Scheduling
AI3691 | Schedule [64] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH64.ActStrTm | 0 |  | Scheduling
AI3692 | Schedule [65] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH65.SchdSt | 0 |  | Scheduling
AI3693 | Schedule [65] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH65.SchdPrio | 1 |  | Scheduling
AI3694 | Schedule [65] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH65.ActStrTm | 0 |  | Scheduling
AI3695 | Schedule [66] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH66.SchdSt | 0 |  | Scheduling
AI3696 | Schedule [66] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH66.SchdPrio | 1 |  | Scheduling
AI3697 | Schedule [66] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH66.ActStrTm | 0 |  | Scheduling
AI3698 | Schedule [67] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH67.SchdSt | 0 |  | Scheduling
AI3699 | Schedule [67] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH67.SchdPrio | 1 |  | Scheduling
AI3700 | Schedule [67] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH67.ActStrTm | 0 |  | Scheduling
AI3701 | Schedule [68] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH68.SchdSt | 0 |  | Scheduling
AI3702 | Schedule [68] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH68.SchdPrio | 1 |  | Scheduling
AI3703 | Schedule [68] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH68.ActStrTm | 0 |  | Scheduling
AI3704 | Schedule [69] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH69.SchdSt | 0 |  | Scheduling
AI3705 | Schedule [69] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH69.SchdPrio | 1 |  | Scheduling
AI3706 | Schedule [69] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH69.ActStrTm | 0 |  | Scheduling
AI3707 | Schedule [70] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH70.SchdSt | 0 |  | Scheduling
AI3708 | Schedule [70] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH70.SchdPrio | 1 |  | Scheduling
AI3709 | Schedule [70] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH70.ActStrTm | 0 |  | Scheduling
AI3710 | Schedule [71] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH71.SchdSt | 0 |  | Scheduling
AI3711 | Schedule [71] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH71.SchdPrio | 1 |  | Scheduling
AI3712 | Schedule [71] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH71.ActStrTm | 0 |  | Scheduling
AI3713 | Schedule [72] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH72.SchdSt | 0 |  | Scheduling
AI3714 | Schedule [72] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH72.SchdPrio | 1 |  | Scheduling
AI3715 | Schedule [72] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH72.ActStrTm | 0 |  | Scheduling
AI3716 | Schedule [73] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH73.SchdSt | 0 |  | Scheduling
AI3717 | Schedule [73] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH73.SchdPrio | 1 |  | Scheduling
AI3718 | Schedule [73] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH73.ActStrTm | 0 |  | Scheduling
AI3719 | Schedule [74] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH74.SchdSt | 0 |  | Scheduling
AI3720 | Schedule [74] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH74.SchdPrio | 1 |  | Scheduling
AI3721 | Schedule [74] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH74.ActStrTm | 0 |  | Scheduling
AI3722 | Schedule [75] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH75.SchdSt | 0 |  | Scheduling
AI3723 | Schedule [75] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH75.SchdPrio | 1 |  | Scheduling
AI3724 | Schedule [75] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH75.ActStrTm | 0 |  | Scheduling
AI3725 | Schedule [76] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH76.SchdSt | 0 |  | Scheduling
AI3726 | Schedule [76] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH76.SchdPrio | 1 |  | Scheduling
AI3727 | Schedule [76] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH76.ActStrTm | 0 |  | Scheduling
AI3728 | Schedule [77] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH77.SchdSt | 0 |  | Scheduling
AI3729 | Schedule [77] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH77.SchdPrio | 1 |  | Scheduling
AI3730 | Schedule [77] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH77.ActStrTm | 0 |  | Scheduling
AI3731 | Schedule [78] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH78.SchdSt | 0 |  | Scheduling
AI3732 | Schedule [78] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH78.SchdPrio | 1 |  | Scheduling
AI3733 | Schedule [78] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH78.ActStrTm | 0 |  | Scheduling
AI3734 | Schedule [79] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH79.SchdSt | 0 |  | Scheduling
AI3735 | Schedule [79] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH79.SchdPrio | 1 |  | Scheduling
AI3736 | Schedule [79] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH79.ActStrTm | 0 |  | Scheduling
AI3737 | Schedule [80] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH80.SchdSt | 0 |  | Scheduling
AI3738 | Schedule [80] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH80.SchdPrio | 1 |  | Scheduling
AI3739 | Schedule [80] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH80.ActStrTm | 0 |  | Scheduling
AI3740 | Schedule [81] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH81.SchdSt | 0 |  | Scheduling
AI3741 | Schedule [81] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH81.SchdPrio | 1 |  | Scheduling
AI3742 | Schedule [81] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH81.ActStrTm | 0 |  | Scheduling
AI3743 | Schedule [82] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH82.SchdSt | 0 |  | Scheduling
AI3744 | Schedule [82] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH82.SchdPrio | 1 |  | Scheduling
AI3745 | Schedule [82] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH82.ActStrTm | 0 |  | Scheduling
AI3746 | Schedule [83] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH83.SchdSt | 0 |  | Scheduling
AI3747 | Schedule [83] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH83.SchdPrio | 1 |  | Scheduling
AI3748 | Schedule [83] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH83.ActStrTm | 0 |  | Scheduling
AI3749 | Schedule [84] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH84.SchdSt | 0 |  | Scheduling
AI3750 | Schedule [84] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH84.SchdPrio | 1 |  | Scheduling
AI3751 | Schedule [84] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH84.ActStrTm | 0 |  | Scheduling
AI3752 | Schedule [85] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH85.SchdSt | 0 |  | Scheduling
AI3753 | Schedule [85] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH85.SchdPrio | 1 |  | Scheduling
AI3754 | Schedule [85] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH85.ActStrTm | 0 |  | Scheduling
AI3755 | Schedule [86] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH86.SchdSt | 0 |  | Scheduling
AI3756 | Schedule [86] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH86.SchdPrio | 1 |  | Scheduling
AI3757 | Schedule [86] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH86.ActStrTm | 0 |  | Scheduling
AI3758 | Schedule [87] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH87.SchdSt | 0 |  | Scheduling
AI3759 | Schedule [87] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH87.SchdPrio | 1 |  | Scheduling
AI3760 | Schedule [87] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH87.ActStrTm | 0 |  | Scheduling
AI3761 | Schedule [88] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH88.SchdSt | 0 |  | Scheduling
AI3762 | Schedule [88] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH88.SchdPrio | 1 |  | Scheduling
AI3763 | Schedule [88] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH88.ActStrTm | 0 |  | Scheduling
AI3764 | Schedule [89] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH89.SchdSt | 0 |  | Scheduling
AI3765 | Schedule [89] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH89.SchdPrio | 1 |  | Scheduling
AI3766 | Schedule [89] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH89.ActStrTm | 0 |  | Scheduling
AI3767 | Schedule [90] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH90.SchdSt | 0 |  | Scheduling
AI3768 | Schedule [90] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH90.SchdPrio | 1 |  | Scheduling
AI3769 | Schedule [90] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH90.ActStrTm | 0 |  | Scheduling
AI3770 | Schedule [91] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH91.SchdSt | 0 |  | Scheduling
AI3771 | Schedule [91] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH91.SchdPrio | 1 |  | Scheduling
AI3772 | Schedule [91] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH91.ActStrTm | 0 |  | Scheduling
AI3773 | Schedule [92] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH92.SchdSt | 0 |  | Scheduling
AI3774 | Schedule [92] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH92.SchdPrio | 1 |  | Scheduling
AI3775 | Schedule [92] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH92.ActStrTm | 0 |  | Scheduling
AI3776 | Schedule [93] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH93.SchdSt | 0 |  | Scheduling
AI3777 | Schedule [93] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH93.SchdPrio | 1 |  | Scheduling
AI3778 | Schedule [93] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH93.ActStrTm | 0 |  | Scheduling
AI3779 | Schedule [94] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH94.SchdSt | 0 |  | Scheduling
AI3780 | Schedule [94] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH94.SchdPrio | 1 |  | Scheduling
AI3781 | Schedule [94] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH94.ActStrTm | 0 |  | Scheduling
AI3782 | Schedule [95] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH95.SchdSt | 0 |  | Scheduling
AI3783 | Schedule [95] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH95.SchdPrio | 1 |  | Scheduling
AI3784 | Schedule [95] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH95.ActStrTm | 0 |  | Scheduling
AI3785 | Schedule [96] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH96.SchdSt | 0 |  | Scheduling
AI3786 | Schedule [96] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH96.SchdPrio | 1 |  | Scheduling
AI3787 | Schedule [96] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH96.ActStrTm | 0 |  | Scheduling
AI3788 | Schedule [97] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH97.SchdSt | 0 |  | Scheduling
AI3789 | Schedule [97] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH97.SchdPrio | 1 |  | Scheduling
AI3790 | Schedule [97] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH97.ActStrTm | 0 |  | Scheduling
AI3791 | Schedule [98] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH98.SchdSt | 0 |  | Scheduling
AI3792 | Schedule [98] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH98.SchdPrio | 1 |  | Scheduling
AI3793 | Schedule [98] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH98.ActStrTm | 0 |  | Scheduling
AI3794 | Schedule [99] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH99.SchdSt | 0 |  | Scheduling
AI3795 | Schedule [99] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH99.SchdPrio | 1 |  | Scheduling
AI3796 | Schedule [99] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH99.ActStrTm | 0 |  | Scheduling
AI3797 | Schedule [100] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH100.SchdSt | 0 |  | Scheduling
AI3798 | Schedule [100] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH100.SchdPrio | 1 |  | Scheduling
AI3799 | Schedule [100] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH100.ActStrTm | 0 |  | Scheduling
AI5000 | Meter #1 Type of Connection Point | 3 | 0 | 99 | 1 | 0 | Enum | Meter1.DECP.EcpConnType | 0 |  | Equipment Data
AI5001 | Meter #1 DER Input/Output Included. <0> unknown <1> metered value does not include input/output of the DER <2> metered value includes all input/output of the DER <3> other | 3 | 0 | 3 | 1 | 0 | Enum | Meter1.DECP.DERMsIncl | 0 |  | Equipment Data
AI5002 | Meter #1 Type of Circuit Phases. <0> unknown <1> Single phase <2> Split phase <3> 2-phase <4> 3-phase delta <5> 3-phase wye <6> 3-phase wye grounded <7> 3-phase / 3-wire (inverter type) <8> 3-phase / 4-wire (inverter type) | 3 | 0 | 8 | 1 | 0 | Enum | Meter1.DECP.PhsConnTyp | 0 |  | Equipment Data
AI5003 | Meter #1 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Meter1.MMXU.ClcTotVA | 0 |  | Equipment Data
AI5004 | Meter #1 Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | Meter1.MMXU.Hz | 0 |  | Equipment Data
AI5005 | Meter #1 Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW | 0 |  | Equipment Data
AI5006 | Meter #1 Active Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsA.mag | 0 |  | Equipment Data
AI5007 | Meter #1 Active Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsB.mag | 0 |  | Equipment Data
AI5008 | Meter #1 Active Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsC.mag | 0 |  | Equipment Data
AI5009 | Meter #1 Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr | 0 |  | Equipment Data
AI5010 | Meter #1 Reactive Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsA.mag | 0 |  | Equipment Data
AI5011 | Meter #1 Reactive Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsB.mag | 0 |  | Equipment Data
AI5012 | Meter #1 Reactive Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsC.mag | 0 |  | Equipment Data
AI5013 | Meter #1 Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF | 0 |  | Equipment Data
AI5014 | Meter #1 Apparent Power | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | Meter1.MMXU.TotVA | 0 |  | Equipment Data
AI5015 | Meter #1 Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.mag | 0 |  | Equipment Data
AI5016 | Meter #1 Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsA.ang | 0 |  | Equipment Data
AI5017 | Meter #1 Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.mag | 0 |  | Equipment Data
AI5018 | Meter #1 Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsB.ang | 0 |  | Equipment Data
AI5019 | Meter #1 Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.mag | 0 |  | Equipment Data
AI5020 | Meter #1 Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsC.ang | 0 |  | Equipment Data
AI5021 | Meter #1 Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.AvPPVPhs | 0 |  | Equipment Data
AI5022 | Meter #1 Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsA.mag | 0 |  | Equipment Data
AI5023 | Meter #1 Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsB.mag | 0 |  | Equipment Data
AI5024 | Meter #1 Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsC.mag | 0 |  | Equipment Data
AI5025 | Meter #1 Active Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.hLim | 0 | AO5000 | Equipment Data
AI5026 | Meter #1 Active Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.lLim | 0 | AO5001 | Equipment Data
AI5027 | Meter #1 Reactive Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.hLim | 0 | AO5002 | Equipment Data
AI5028 | Meter #1 Reactive Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.lLim | 0 | AO5003 | Equipment Data
AI5029 | Meter #1 Power Factor – High Threshold | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.hLim | 0 | AO5004 | Equipment Data
AI5030 | Meter #1 Power Factor – Low Threshold | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.lLim | 0 | AO5005 | Equipment Data
AI5031 | Meter #1 Phase A Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.hLim | 0 | AO5006 | Equipment Data
AI5032 | Meter #1 Phase A Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.lLim | 0 | AO5007 | Equipment Data
AI5033 | Meter #1 Phase B Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.hLim | 0 | AO5008 | Equipment Data
AI5034 | Meter #1 Phase B Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.lLim | 0 | AO5009 | Equipment Data
AI5035 | Meter #1 Phase C Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.hLim | 0 | AO5010 | Equipment Data
AI5036 | Meter #1 Phase C Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.lLim | 0 | AO5011 | Equipment Data
AI10000 | DER Unit #1 Unit Type. Enumeration: <0> unknown <1> Diesel / gas engine <2> Gas Turbine engine <3> PV <4> PV plus Storage <5> Lithium Ion Battery Storage <6> Fuel cell <7> Hydro generator <8> Wind turbine <9> Flow battery storage <10> Air compression storage <11> Flywheel storage <12> Capacitor storage <13> Vehicle-to-Grid (V2G) <50> Mixed, hybrid DER <98> Not applicable / Unknown <99> Other | 3 | 0 | 99 | 1 | 0 | Enum | DER_Unit1.DGEN.DERTyp | 0 |  | Equipment Data
AI10001 | DER Unit #1 Nameplate Energy Capacity. Nameplate energy capacity for the DER unit expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DER_Unit1.DGEN.WMeteraxRtg | 0 |  | Equipment Data
AI10002 | IEEE 1547 Normal Operating Performance Category. <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DER_Unit1.DGEN.RegCls.1 | 0 |  | Equipment Data
AI10003 | IEEE 1547 Abnormal Operating Performance Category. <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DER_Unit1.DGEN.RegCls.2 | 0 |  | Equipment Data
AI10004 | DER Unit #1 Maximum Apparent Generation Power | 2 | 0 | 2147483647 | 1 | 0 | VA | DER_Unit1.DGEN.VAMax | 0 |  | Equipment Data
AI10005 | DER Unit #1 Maximum Apparent Charging Power | 2 | -2147483648 | 0 | 1 | 0 | VA | DER_Unit1.DSTO.ChaVAMax | 0 |  | Equipment Data
AI10006 | DER Unit #1 Operational Time. Time in seconds since commissioning. | 3 | 0 | 2147483647 | 1 | 0 | Seconds | DER_Unit1.DGEN.GnOpTms | 0 |  | Equipment Data
AI10007 | DER Unit #1 Connection Time. Number of hours the DER unit has been connected to the power system. | 3 | 0 | 2147483647 | 1 | 0 | Hours | DER_Unit1.DGEN.OpTmRs | 0 |  | Equipment Data
AI10008 | DER Unit #1 Available Active Generation Power | 1 | 0 | 2147483647 | 1 | 0 | W | DER_Unit1.DSTO.WAvlUp | 0 |  | Equipment Data
AI10009 | DER Unit #1 Available Active Charging Power | 1 | -2147483648 | 0 | 1 | 0 | W | DER_Unit1.DSTO.WAvlDn | 0 |  | Equipment Data
AI10010 | DER Unit #1 Available Reactive Injection Power | 1 | 0 | 2147483647 | 1 | 0 | Vars | DER_Unit1.DGEN.TotIvarAvl | 0 |  | Equipment Data
AI10011 | DER Unit #1 Available Reactive Absorption Power | 1 | -2147483648 | 0 | 1 | 0 | Vars | DER_Unit1.DGEN.TotAvarAvl | 0 |  | Equipment Data
AI10012 | DER Unit #1 Non-impacting Injection VArs Available. VArs that can be injected without impacting Active Power Output | 2 | 0 | 2147483647 | 1 | 0 | Vars | DER_Unit1.DGEN.IvarAvl | 0 |  | Equipment Data
AI10013 | DER Unit #1 Non-impacting Absorption VArs Available. VArs that can be absorbed without impacting Active Power Output | 2 | -2147483648 | 0 | 1 | 0 | Vars | DER_Unit1.DGEN.AvarAvl | 0 |  | Equipment Data
AI10014 | DER Unit #1 Link to Meter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | DER_Unit1.MESA.MeterNum | 0 |  | Equipment Data
AI15000 | Inverter #1 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Inverter1.MMXU.ClcTotVA | 0 |  | Equipment Data
AI15001 | Inverter #1 Active Power Target | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter1.DINV.WTgt | 0 |  | Equipment Data
AI15002 | Inverter #1 Reactive Power Target | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter1.DINV.VArTgtPct | 0 |  | Equipment Data
AI15003 | Inverter #1 Active Power. Present active power measurement. | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW | 0 |  | Equipment Data
AI15004 | Inverter #1 Reactive Power. Present reactive power measurement. | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr | 0 |  | Equipment Data
AI15005 | Inverter #1 Power Factor | 2 | -100 | 100 | 0.01 | 0 | None | Inverter1.MMXU.TotPF | 0 |  | Equipment Data
AI15006 | Inverter #1 Apparent Power | 2 | -2147483648 | 2147483647 | 1 | 0 | VA | Inverter1.MMXU.TotVA | 0 |  | Equipment Data
AI15007 | Inverter #1 DC Input Power | 3 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt | 0 |  | Equipment Data
AI15008 | Inverter #1 DC Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol | 0 |  | Equipment Data
AI15009 | Inverter #1 DC Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp | 0 |  | Equipment Data
AI15010 | Inverter #1 Average Line to Neutral Voltage. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PhV | 0 |  | Equipment Data
AI15011 | Inverter #1 Voltage Phase A to B. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsAB | 0 |  | Equipment Data
AI15012 | Inverter #1 Voltage Phase B to C. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsBC | 0 |  | Equipment Data
AI15013 | Inverter #1 Voltage Phase C to A. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsCA | 0 |  | Equipment Data
AI15014 | Inverter #1 AC Current. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A | 0 |  | Equipment Data
AI15015 | Inverter #1 Current Phase A. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsA | 0 |  | Equipment Data
AI15016 | Inverter #1 Current Phase B. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsB | 0 |  | Equipment Data
AI15017 | Inverter #1 Current Phase C. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsC | 0 |  | Equipment Data
AI15018 | Inverter #1 Internal (Cabinet) Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.EnclTmp | 0 |  | Equipment Data
AI15019 | Inverter #1 Heat Sink Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.HeatSinkTmp | 0 |  | Equipment Data
AI15020 | Inverter #1 Transformer Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.TrfTmp | 0 |  | Equipment Data
AI15021 | Inverter #1 Active Power Output - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.hLim | 0 | AO15000 | Equipment Data
AI15022 | Inverter #1 Active Power Output - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.lLim | 0 | AO15001 | Equipment Data
AI15023 | Inverter #1 Reactive Power Output – High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.hLim | 0 | AO15002 | Equipment Data
AI15024 | Inverter #1 Reactive Power Output – Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.lLim | 0 | AO15003 | Equipment Data
AI15025 | Inverter #1 Current Output Frequency – High Threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.hLim | 0 | AO15004 | Equipment Data
AI15026 | Inverter #1 Current Output Frequency – Low Threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.lLim | 0 | AO15005 | Equipment Data
AI15027 | Inverter #1 DC Inverter Input Power - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.hLim | 0 | AO15006 | Equipment Data
AI15028 | Inverter #1 DC Inverter Input Power - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.lLim | 0 | AO15007 | Equipment Data
AI15029 | Inverter #1 DC Current Available – High Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp.RangeC.hLim | 0 | AO15008 | Equipment Data
AI15030 | Inverter #1 DC Current Available – Low Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp.RangeC.lLim | 0 | AO15009 | Equipment Data
AI15031 | Inverter #1 DC Voltage Between DER System and Inverter – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.hLim | 0 | AO15010 | Equipment Data
AI15032 | Inverter #1 DC Voltage Between DER System and Inverter – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.lLim | 0 | AO15011 | Equipment Data
AI15033 | Inverter #1 Link to DER Unit # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Inverter1.MESA.DER_UnitNum | 0 |  | Equipment Data
AI15068 | Inverter #3 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Inverter3.MMXU.ClcTotVA | 0 |  | Equipment Data
AI15069 | Inverter #3 Active Power Target | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter3.DINV.WTgt | 0 |  | Equipment Data
AI15070 | Inverter #3 Reactive Power Target | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter3.DINV.VArTgtPct | 0 |  | Equipment Data
AI15071 | Inverter #3 Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter3.MMXU.TotW | 0 |  | Equipment Data
AI15072 | Inverter #3 Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter3.MMXU.TotVAr | 0 |  | Equipment Data
AI15073 | Inverter #3 Power Factor | 2 | -100 | 100 | 0.01 | 0 | None | Inverter3.MMXU.TotPF | 0 |  | Equipment Data
AI15074 | Inverter #3 Apparent Power | 2 | -2147483648 | 2147483647 | 1 | 0 | VA | Inverter3.MMXU.TotVA | 0 |  | Equipment Data
AI15075 | Inverer #3 DC Input Power | 3 | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMDC.Watt | 0 |  | Equipment Data
AI15076 | Inverter #3 DC Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMDC.Vol | 0 |  | Equipment Data
AI15077 | Inverter #3 DC Current | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMDC.Amp | 0 |  | Equipment Data
AI15078 | Inverter #3 Average Line to Neutral Voltage. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMXU.PhV | 0 |  | Equipment Data
AI15079 | Inverter #3 Voltage Phase A to B. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMXU.PPV.phsAB | 0 |  | Equipment Data
AI15080 | Inverter #3 Voltage Phase B to C. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMXU.PPV.phsBC | 0 |  | Equipment Data
AI15081 | Inverter #3 Voltage Phase C to A. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMXU.PPV.phsCA | 0 |  | Equipment Data
AI15082 | Inverter #3 Current. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMXU.A | 0 |  | Equipment Data
AI15083 | Inverter #3 Current Phase A. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMXU.A.phsA | 0 |  | Equipment Data
AI15084 | Inverter #3 Current Phase B. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMXU.A.phsB | 0 |  | Equipment Data
AI15085 | Inverter #3 Current Phase C. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMXU.A.phsC | 0 |  | Equipment Data
AI15086 | Inverter #3 Internal (Cabinet) Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter3.DINV.EnclTmp | 0 |  | Equipment Data
AI15087 | Inverter #3 Heat Sink Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter3.DINV.HeatSinkTmp | 0 |  | Equipment Data
AI15088 | Inverter #3 Transformer Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter3.DINV.TrfTmp | 0 |  | Equipment Data
AI15089 | Inverter #3 Active Power Output - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMXU.TotW.RangeC.hLim | 0 | AO15024 | Equipment Data
AI15090 | Inverter #3 Active Power Output - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMXU.TotW.RangeC.lLim | 0 | AO15025 | Equipment Data
AI15091 | Inverter #3 Reactive Power Output – High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter3.MMXU.TotVAr.rangeC.hLim | 0 | AO15026 | Equipment Data
AI15092 | Inverter #3 Reactive Power Output – Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter3.MMXU.TotVAr.rangeC.lLim | 0 | AO15027 | Equipment Data
AI15093 | Inverter #3 Current Output Frequency – High Threshold | 2 | 0 | 70000 | 0.001 | 0 | Hz | Inverter3.MMXU.Hz.rangeC.hLim | 0 | AO15028 | Equipment Data
AI15094 | Inverter #3 Current Output Frequency – Low Threshold | 2 | 0 | 70000 | 0.001 | 0 | Hz | Inverter3.MMXU.Hz.rangeC.lLim | 0 | AO15029 | Equipment Data
AI15095 | Inverter #3 DC Inverter Input Power - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMDC.Watt.RangeC.hLim | 0 | AO15030 | Equipment Data
AI15096 | Inverter #3 DC Inverter Input Power - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter3.MMDC.Watt.RangeC.lLim | 0 | AO15031 | Equipment Data
AI15097 | Inverter #3 DC Current Available – High Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMDC.Amp.RangeC.hLim | 0 | AO15032 | Equipment Data
AI15098 | Inverter #3 DC Current Available – Low Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter3.MMDC.Amp.RangeC.lLim | 0 | AO15033 | Equipment Data
AI15099 | Inverter #3 DC Voltage Between DER System and Inverter – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMDC.Vol.RangeC.hLim | 0 | AO15034 | Equipment Data
AI15100 | Inverter #3 DC Voltage Between DER System and Inverter – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter3.MMDC.Vol.RangeC.lLim | 0 | AO15035 | Equipment Data
AI15101 | Inverter #3 Link to DER Unit # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Inverter3.MESA.DER_UnitNum | 0 |  | Equipment Data
AI20000 | Battery Bank #1 Type of Storage. <0> n/a, Unknown <1> Lead-acid <2> Nickel-metal hydrate (NiMH) <3> Nickel-cadmium (NiCad) <4> LitInverterum <5> Carbon zinc <6> Zinc chloride <7> Alkaline <8> Rechargeable alkaline <9> Sodium sulphur (NaS) <10> Flow <99> Other | 2 | 0 | 99 | 1 | 0 | Enum | Battery1.DBAT.BatTyp | 0 |  | Equipment Data
AI20001 | Battery Bank #1 Nameplate Actual Capacity Rating. The actual total capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery1.DBAT.WMeteraxRtg | 0 |  | Equipment Data
AI20002 | Battery Bank #1 Effective Capacity. The present effective capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery1.DBAT.EffWh | 0 |  | Equipment Data
AI20003 | Battery Bank #1 Minimum Reserve for Storage. As a percentage of the nominal useable storage (DBAT.CapWhUseRtg) | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.UseWMeterinPct | 0 |  | Equipment Data
AI20004 | Battery Bank #1 Maximum Reserve for Storage. As a percentage of the nominal useable storage (DBAT.CapWhUseRtg). Expressed as a delta from the maximum usable capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.UseWMeteraxPct | 0 |  | Equipment Data
AI20005 | Battery Bank #1 Battery State. <0> n/a, Unknown <1> Disconnected <2> Initializing <3> Connected <4> Standby <5> SOC Protection <6> Suspending <99> Fault | 2 | 0 | 99 | 1 | 0 | Enum | Battery1.DBAT.BatSt | 0 |  | Equipment Data
AI20006 | Battery Bank #1 Actual State of Charge. Currently available energy in the battery, as a percentage of the effective capacity. | 3 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.SocWh | 0 |  | Equipment Data
AI20007 | Battery Bank #1 State of Health. The ratio (expressed as a percentage) of the current rating of the battery with respect to the nameplate rating of the battery and end-of-life criteria. The rating of the battery may include one or more battery parameters that are selected as appropriate for the application and implementation. These parameters often include the energy capacity, but could also incorporate other measurements. | 1 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.EffWhPct | 0 |  | Equipment Data
AI20008 | Battery Bank #1 External Battery Voltage. Voltage measured between battery charger and battery. | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVol | 0 |  | Equipment Data
AI20009 | Battery Bank #1 Internal Battery Voltage. Internal voltage measurement. | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVol | 0 |  | Equipment Data
AI20010 | Battery Bank #1 Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Battery1.DBAT.Amp | 0 |  | Equipment Data
AI20011 | Battery Bank #1 Power | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Watts | Battery1.DBAT.Watt | 0 |  | Equipment Data
AI20012 | Battery Bank #1 Minimum Cell Voltage. Minimum cell voltage measurement of all cells in the bank. | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery1.SBAT.CelVolLo | 0 |  | Equipment Data
AI20013 | Battery Bank #1 Maximum Cell Voltage. Maximum cell voltage measurement of all cells in the bank. | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery1.SBAT.CelVolInverter | 0 |  | Equipment Data
AI20014 | Battery Bank #1 Minimum Temperature. Minimum temperature measurement for all sensors in the bank. | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.SBAT.CelTmpMin | 0 |  | Equipment Data
AI20015 | Battery Bank #1 Maximum Temperature. Maximum temperature measurement for all sensors in the bank. | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.SBAT.CelTmpMax | 0 |  | Equipment Data
AI20016 | Battery Bank #1 External Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.DBAT.ExtTmp | 0 |  | Equipment Data
AI20017 | Battery Bank #1 Internal Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.DBAT.IntnTmp | 0 |  | Equipment Data
AI20018 | Battery Bank #1 Charge Current Limit. Instantaneous current limit on charging. | 1 | -2147483648 | 0 | 0.1 | 0 | Amps | Battery1.DBAT.ChaAmpLim | 0 |  | Equipment Data
AI20019 | Battery Bank #1 Discharge Current Limit. Instantaneous current limit on discharging. | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | Battery1.DBAT.DschAmpLim | 0 |  | Equipment Data
AI20020 | Battery Bank #1 Minimum Voltage Limit. Instantaneous minimum voltage limit. | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.VolMinLim | 0 |  | Equipment Data
AI20021 | Battery Bank #1 Maximum Voltage Limit. Instantaneous maximum voltage limit. | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.VolMaxLim | 0 |  | Equipment Data
AI20022 | Battery Bank #1 Connected String Count. Number of strings in the bank that are currently connected. | 1 | 0 | 2147483647 | 1 | 0 | n/a | Battery1.DBAT.CelStrgCnt | 0 |  | Equipment Data
AI20023 | Battery Bank #1 External Voltage - High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolInverterAls | 0 | AO20000 | Equipment Data
AI20024 | Battery Bank #1 External Voltage - Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolLoAls | 0 | AO20001 | Equipment Data
AI20025 | Battery Bank #1 Internal Voltage – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolInverterAls | 0 | AO20002 | Equipment Data
AI20026 | Battery Bank #1 Internal Voltage – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolLoAls | 0 | AO20003 | Equipment Data
AI20027 | Battery Bank #1 Link to Inverter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Battery1.MESA.InverterNum | 0 |  | Equipment Data
AI20056 | Battery Bank #3 Type of Storage. <0> n/a, Unknown <1> Lead-acid <2> Nickel-metal hydrate (NiMH) <3> Nickel-cadmium (NiCad) <4> LitInverterum <5> Carbon zinc <6> Zinc chloride <7> Alkaline <8> Rechargeable alkaline <9> Sodium sulphur (NaS) <10> Flow <99> Other | 2 | 0 | 99 | 1 | 0 | Enum | Battery3.DBAT.BatTyp | 0 |  | Equipment Data
AI20057 | Battery Bank #3 Nameplate Actual Capacity Rating. The actual total capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery3.DBAT.WMeteraxRtg | 0 |  | Equipment Data
AI20058 | Battery Bank #3 Effective Capacity. The present effective capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery3.DBAT.EffWh | 0 |  | Equipment Data
AI20059 | Battery Bank #3 Minimum Reserve for Storage | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery3.DBAT.UseWMeterinPct | 0 |  | Equipment Data
AI20060 | Battery Bank #3 Maximum Reserve for Storage. | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery3.DBAT.UseWMeteraxPct | 0 |  | Equipment Data
AI20061 | Battery Bank #3 Battery State. <0> n/a, Unknown <1> Disconnected <2> Initializing <3> Connected <4> Standby <5> SOC Protection <6> Suspending <99> Fault | 2 | 0 | 99 | 1 | 0 | Enum | Battery3.DBAT.BatSt | 0 |  | Equipment Data
AI20062 | Battery Bank #3 External Battery Voltage | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.SocWh | 0 |  | Equipment Data
AI20063 | Battery Bank #3 Internal Battery Voltage | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.EffWhPct | 0 |  | Equipment Data
AI20064 | Battery Bank #3 State of Charge | 3 | 0 | 1000 | 0.1 | 0 | Percent | Battery3.DBAT.ExtVol | 0 |  | Equipment Data
AI20065 | Battery Bank #3 State of Health | 1 | 0 | 1000 | 0.1 | 0 | Percent | Battery3.DBAT.IntnVol | 0 |  | Equipment Data
AI20066 | Battery Bank #3 Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Battery3.DBAT.Amp | 0 |  | Equipment Data
AI20067 | Battery Bank #3 Power | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Watts | Battery3.DBAT.Watt | 0 |  | Equipment Data
AI20068 | Battery Bank #3 Minimum Cell Voltage | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery3.SBAT.CelVolLo | 0 |  | Equipment Data
AI20069 | Battery Bank #3 Maximum Cell Voltage | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery3.SBAT.CelVolInverter | 0 |  | Equipment Data
AI20070 | Battery Bank #3 Minimum Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery3.SBAT.CelTmpMin | 0 |  | Equipment Data
AI20071 | Battery Bank #3 Maximum Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery3.SBAT.CelTmpMax | 0 |  | Equipment Data
AI20072 | Battery Bank #3 External Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery3.DBAT.ExtTmp | 0 |  | Equipment Data
AI20073 | Battery Bank #3 Internal Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery3.DBAT.IntnTmp | 0 |  | Equipment Data
AI20074 | Battery Bank #3 Charge Current Limit | 1 | -2147483648 | 0 | 0.1 | 0 | Amps | Battery3.DBAT.ChaAmpLim | 0 |  | Equipment Data
AI20075 | Battery Bank #3 Discharge Current Limit | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | Battery3.DBAT.DschAmpLim | 0 |  | Equipment Data
AI20076 | Battery Bank #3 Minimum Voltage Limit | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.VolMinLim | 0 |  | Equipment Data
AI20077 | Battery Bank #3 Maximum Voltage Limit | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.VolMaxLim | 0 |  | Equipment Data
AI20078 | Battery Bank #3 Connected String Count | 1 | 0 | 2147483647 | 1 | 0 | n/a | Battery3.DBAT.CelStrgCnt | 0 |  | Equipment Data
AI20079 | Battery Bank #3 External Voltage - High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.ExtVolInverterAls | 0 | AO20008 | Equipment Data
AI20080 | Battery Bank #3 External Voltage - Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.ExtVolLoAls | 0 | AO20009 | Equipment Data
AI20081 | Battery Bank #3 Internal Voltage – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.IntnVolInverterAls | 0 | AO20010 | Equipment Data
AI20082 | Battery Bank #3 Internal Voltage – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery3.DBAT.IntnVolLoAls | 0 | AO20011 | Equipment Data
AI20083 | Battery Bank #3 Link to Inverter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Battery3.MESA.InverterNum | 0 |  | Equipment Data
AI30000 | Volt-Watt Adv Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVWC1.ModPrio | 0 | AO30000 | Volt-Watt Advanced | C: For Function
AI30001 | Volt-Watt Adv Enabling Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.WinTms | 0 | AO30001 | Volt-Watt Advanced
AI30002 | Volt-Watt Adv Enabling Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.RmpTms | 0 | AO30002 | Volt-Watt Advanced
AI30003 | Volt-Watt Adv Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.RvrtTms | 0 | AO30003 | Volt-Watt Advanced
AI30004 | Volt-Watt Adv Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | 0 | AO30004 | Volt-Watt Advanced | C: For Function
AI30005 | Volt-Watt Adv Reference Voltage Input. Voltage measurement read from the signal meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.MMXN.Vol | 0 |  | Volt-Watt Advanced | C: For Function
AI30006 | Volt-Watt Adv High Start Voltage Threshold. Voltage threshold for starting high voltage events. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | 0 | AO30005 | Volt-Watt Advanced | C: For Function
AI30007 | Volt-Watt Adv High Stop Voltage Threshold. Voltage threshold for stopping high voltage events. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStop | 0 | AO30006 | Volt-Watt Advanced
AI30008 | Volt-Watt Adv Low Start Voltage Threshold. Voltage threshold for starting low voltage events. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | 0 | AO30007 | Volt-Watt Advanced | C: For Function
AI30009 | Volt-Watt Adv Low Stop Voltage Threshold. Voltage threshold for stopping low voltage events. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStop | 0 | AO30008 | Volt-Watt Advanced
AI30010 | Volt-Watt Adv Start Delay. Delay at start thresholds to verify voltage exceeds that threshold. | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DVWC1.ActStrDlTmms | 0 | AO30009 | Volt-Watt Advanced
AI30011 | Volt-Watt Adv Stop Delay. Delay at stop thresholds to verify voltage has returned to normal. | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DVWC1.ActStopDlTmms | 0 | AO30010 | Volt-Watt Advanced
AI30012 | Volt-Watt Adv Curve Index. Index of the Volt-Watt Adv curve that should be used by the m | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | 0 | AO30011 | Volt-Watt Advanced | C: For Function
AI30013 | Volt-Watt Adv Attempted Output. Maximum active power the outstation is permitted to generate or absorb based on the voltage level and gradient. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DVWC1.ReqWLim | 0 |  | Volt-Watt Advanced | C: For Function
AI30014 | Volt-Watt Adv Filter Time (Seconds) | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.FilTms | 0 | AO30012 | Volt-Watt Advanced
AI30015 | Volt-Watt Adv Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.1 | 0 | AO30013 | Volt-Watt Advanced
AI30016 | Volt-Watt Adv Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.2 | 0 | AO30014 | Volt-Watt Advanced
AI30017 | Volt-Watt Adv Discharging Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuRte | 0 | AO30015 | Volt-Watt Advanced | C: For Function
AI30018 | Volt-Watt Adv Discharging Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdRte | 0 | AO30016 | Volt-Watt Advanced | C: For Function
AI30019 | Volt-Watt Adv Charging Ramp Up Rate. Maximum charging ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuChaRte | 0 | AO30017 | Volt-Watt Advanced | C: For Function
AI30020 | Volt-Watt Adv Charging Ramp Down Rate. Maximum charging ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdChaRte | 0 | AO30018 | Volt-Watt Advanced | C: For Function
AI30021 | Volt-Watt Adv Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMinPct | 0 | AO30019 | Volt-Watt Advanced | C: For Function
AI30022 | Volt-Watt Adv Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMaxPct | 0 | AO30020 | Volt-Watt Advanced | C: For Function
AI30050 | Synthetic Inertia Priority | 2 | 0 | 100 | 1 | 0 | n/a | DSYN.ModPrio | 0 | AO30050 | Synthetic Inertia
AI30051 | Synthetic Inertia Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DSYN.WinTms | 0 | AO30051 | Synthetic Inertia
AI30052 | Synthetic Inertia Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DSYN.RmpTms | 0 | AO30052 | Synthetic Inertia
AI30053 | Synthetic Inertia Reversion Timeout | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DSYN.RvrtTms | 0 | AO30053 | Synthetic Inertia
AI30054 | Synthetic Inertia Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DSYN.EcpRef | 0 | AO30054 | Synthetic Inertia | C: For Function
AI30055 | Set the Synthetic Inertia Discharge Ramp Up Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.DschRpuPct | 0 | AO30055 | Synthetic Inertia | C: For Function
AI30056 | Set the Synthetic Inertia Discharge Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.DschRpdPct | 0 | AO30056 | Synthetic Inertia | C: For Function
AI30057 | Set the Synthetic Inertia Charge Ramp Up Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.ChaRpuPct | 0 | AO30057 | Synthetic Inertia | C: For Function
AI30058 | Set the Synthetic Inertia Charge Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.ChaRpdPct | 0 | AO30058 | Synthetic Inertia | C: For Function
AI30059 | Set the Synthetic Inertia Derivative Factor | 2 | 0 | 2147483647 | 1 | 0 | Percent W per Hz per sec | DSYN.RcfWHzTmPct | 0 | AO30059 | Synthetic Inertia | C: For Function
AI30060 | Set the Synthetic Inertia Lower Deadband | 2 | 0 | 2147483647 | 1 | 0 | Hz | DSYN.DbHzMin | 0 | AO30060 | Synthetic Inertia | C: For Function
AI30061 | Set the Synthetic Inertia Upper Deadband | 2 | 0 | 2147483647 | 1 | 0 | Hz | DSYN.DbHzMax | 0 | AO30061 | Synthetic Inertia | C: For Function
VP | Vendor Points | [7 empty] | 0
AI65000 | SCADA, Configuration - (Base-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScdBo | 65535 |  | SCADA, Config
AI65001 | SCADA, Configuration - (Base-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScdBi | 65535 |  | SCADA, Config
AI65002 | SCADA, Configuration - (Base-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScdAo | 65535 |  | SCADA, Config
AI65003 | SCADA, Configuration - (Base-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScdAi | 65535 |  | SCADA, Config
AI65004 | Functions (Fn-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.FunBo | 65535 |  | Functions
AI65005 | Functions (Fn-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.FunBi | 65535 |  | Functions
AI65006 | Functions (Fn-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.FunAo | 65535 |  | Functions
AI65007 | Functions (Fn-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.FunAi | 65535 |  | Functions
AI65008 | Curves (Crv-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.CrvBo | 65535 |  | Curves
AI65009 | Curves (Crv-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.CrvBi | 65535 |  | Curves
AI65010 | Curves (Crv-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.CrvAo | 65535 |  | Curves
AI65011 | Curves (Crv-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.CrvAi | 65535 |  | Curves
AI65012 | System Meter (Mtr-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MtrBo | 65535 |  | System Meter
AI65013 | System Meter (Mtr-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MtrBi | 65535 |  | System Meter
AI65014 | System Meter (Mtr-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MtrAo | 65535 |  | System Meter
AI65015 | System Meter (Mtr-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MtrAi | 65535 |  | System Meter
AI65016 | Gap #1 (Gap1-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap1Bo | 65535 |  | Gap #1
AI65017 | Gap #1 (Gap1-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap1Bi | 65535 |  | Gap #1
AI65018 | Gap #1 (Gap1-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap1Ao | 65535 |  | Gap #1
AI65019 | Gap #1 (Gap1-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap1Ai | 65535 |  | Gap #1
AI65020 | Backward Compatible Schedules (Sch-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScBatteryo | 65535 |  | Schedules
AI65021 | Backward Compatible Schedules (Sch-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScBatteryi | 65535 |  | Schedules
AI65022 | Backward Compatible Schedules (Sch-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.SchAo | 65535 |  | Schedules
AI65023 | Backward Compatible Schedules (Sch-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.SchAi | 65535 |  | Schedules
AI65024 | Schedules (Sch-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScBatteryo | 65535 |  | Schedules
AI65025 | Schedules (Sch-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ScBatteryi | 65535 |  | Schedules
AI65026 | Schedules (Sch-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.SchAo | 65535 |  | Schedules
AI65027 | Schedules (Sch-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.SchAi | 65535 |  | Schedules
AI65028 | Gap #2 (Gap2-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap2Bo | 65535 |  | Gap #2
AI65029 | Gap #2 (Gap2-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap2Bi | 65535 |  | Gap #2
AI65030 | Gap #2 (Gap2-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap2Ao | 65535 |  | Gap #2
AI65031 | Gap #2 (Gap2-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.Gap2Ai | 65535 |  | Gap #2
AI65032 | Meters (Meter-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MeterBo | 65535 |  | Meters
AI65033 | Meters (Meter-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MeterBi | 65535 |  | Meters
AI65034 | Meters (Meter-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MeterAo | 65535 |  | Meters
AI65035 | Meters (Meter-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.MeterAi | 65535 |  | Meters
AI65036 | DER Units (DER_Unit-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.DER_UnitBo | 65535 |  | DER_Units
AI65037 | DER Units (DER_Unit-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.DER_UnitBi | 65535 |  | DER_Units
AI65038 | DER Units (DER_Unit-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.DER_UnitAo | 65535 |  | DER_Units
AI65039 | DER Units (DER_Unit-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.DER_UnitAi | 65535 |  | DER_Units
AI65040 | Inverters (Inverter-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.InverterBo | 65535 |  | Inverters
AI65041 | Inverters (Inverter-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.InverterBi | 65535 |  | Inverters
AI65042 | Inverters (Inverter-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.InverterAo | 65535 |  | Inverters
AI65043 | Inverters (Inverter-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.InverterAi | 65535 |  | Inverters
AI65044 | Batteries (Battery-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.BatteryBo | 65535 |  | Batteries
AI65045 | Batteries (Battery-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.BatteryBi | 65535 |  | Batteries
AI65046 | Batteries (Battery-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.BatteryAo | 65535 |  | Batteries
AI65047 | Batteries (Battery-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.BatteryAi | 65535 |  | Batteries
AI65048 | Experimental (Exp-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ExpBo | 65535 |  | Experimental
AI65049 | Experimental (Exp-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ExpBi | 65535 |  | Experimental
AI65050 | Experimental (Exp-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ExpAo | 65535 |  | Experimental
AI65051 | Experimental (Exp-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.ExpAi | 65535 |  | Experimental
AI65052 | Vendor Points (Ven-BO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.VenBo | 65535 |  | Vendor
AI65053 | Vendor Points (Ven-BI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.VenBi | 65535 |  | Vendor
AI65054 | Vendor Points (Ven-AO) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.VenAo | 65535 |  | Vendor
AI65055 | Vendor Points (Ven-AI) starting index | not in Class 0 | 65535 | 65535 | 1 | 0 | Index | Index.VenAi | 65535 |  | Vendor
AI65056 | Number of meters (Meter) | not in Class 0 | 65535 | 65535 | 1 | 0 | Number of Units | Num.Meter | 65535 |  | Number of Units
AI65057 | Number of DER Units (DER_Unit) | not in Class 0 | 65535 | 65535 | 1 | 0 | Number of Units | Num.DER_Unit | 65535 |  | Number of Units
AI65058 | Number of Inverters (Inverter) | not in Class 0 | 65535 | 65535 | 1 | 0 | Number of Units | Num.Inverter | 65535 |  | Number of Units
AI65059 | Number of Batteries (Battery) | not in Class 0 | 65535 | 65535 | 1 | 0 | Number of Units | Num.Battery | 65535 |  | Number of Units

## CTR
DNP3 Point Index | Name / Description | Default Class Assigned to Counter Events | Frozen Counter Exists (Yes or No) | Default Class Assigned to Frozen Counter Events | IEC 61850 | Additional Information |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Purpose/Mode/ Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
CTR0 | System Active Energy Delivered. Measured in watt-hours. | n/a | Yes | 3 | MMTR.SupWh | Metering
CTR1 | System Active Energy Received. Measured in watt-hours. | n/a | Yes | 3 | MMTR.DmdWh | Metering
CTR2 | System Reactive Energy Delivered. Measured in VAr-hours. | n/a | Yes | 3 | MMTR.SupVArh | Metering
CTR3 | System Reactive Energy Received. Measured in VAr-hours. | n/a | Yes | 3 | MMTR.DmdVArh | Metering
CTR5000 | Meter #1 Active Energy Delivered. Measured in watt-hours. | n/a | Yes | 3 | HM1MMTR.SupWh | Metering
CTR5001 | Meter #1 Active Energy Received. Measured in watt-hours. | n/a | Yes | 3 | HM1MMTR.DmdWh | Metering
CTR5002 | Meter #1 Reactive Energy Delivered. Measured in VAr-hours. | n/a | Yes | 3 | HM1MMTR.SupVArh | Metering
CTR5003 | Meter #1 Reactive Energy Received. Measured in VAr-hours. | n/a | Yes | 3 | HM1MMTR.DmdVArh | Metering

## System Diagrams
Naming of Data Objects