## Key
IEEE 1815.2 Standard Profile Companion Data Point Tables: Version 1.1
DNP3 Points |  | Start Index | BO | BI | AO | AI | CTR
SCADA
Configuration & Control Points |  | 0 | 0 | 0 | 0 | 0 | 0
Functions |  | 0 | 12 | 31 | 22 | 71 | 0 |  | Configuration Settings
Curves | Max of 100 x,y pairs per Curve | 0 | 0 | 107 | 244 | 328 | 0 |  | Allocate the number of curves and the maximum number of points per curve
System Meter |  | 0 | 0 | 94 | 449 | 533 | 0
Extensions beyond DNP3 AN2018-001 |  | 0 | 42 | 108 | 461 | 569 | 0
Gap #1 | Reserved for future extensions | x | 44 | 111 | 476 | 586
Schedules
Schedules (2 items/step) | Time offset, value (for backwards compat) | 2000 | 2000 | 2000 | 2000 | 2000 |  |  | Allocate number of schedules and the maximum points per schedule
Schedule Status (2 items) | Schedule Status of first 100 | 2300 |  | 2300 |  | 2300
Schedules (4 items/step) | Time offset, Action type, AO or BO Index, & Value | 3000 | 3000 | 3000 | 3000 | 3000
Schedule Status (4 items) | Schedule Status of first 100 | 3500 | - | 3500 | - | 3500
Gap #2 | Reserved for future extensions | 4000
Equipment Points |  |  | BO | BI | AO | AI | CTR | Enter Maximum # of Devices
Meters | Start of additional meter points | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 1 | No. of Meters
| mh(1) set of points per meter |  | 0 | 13 | 12 | 37 | 4
| mh(n) total length of points |  | 0 | 39 | 36 | 111 | 12
DER Units | Start of DER unit points. | 10000 | 10000 | 10000 | 10000 | 10000 |  | 1 | No. DER Units
| duh(1) set of points per DER unit |  | 0 | 4 | 0 | 15 | 0
| duh(n) total length of points |  | 0 | 28 | 0 | 98
Inverters | Start of inverter points. | 15000 | 15000 | 15000 | 15000 | 15000 |  | 1 | No. Inverters
| ihh(1) set of points per inverter |  | 0 | 35 | 12 | 34 | 0
| ihh(n) total length of points |  | 0 | 70 | 24 | 66
Batteries | Start of battery points. | 20000 | 20000 | 20000 | 20000 | 20000 |  | 1 | No. Batteries
| bhh(1) set of points per battery |  | 0 | 54 | 4 | 28 | 0 | For each meter, DER unit, inverter, and battery, additional historical data rows need to be added in the spreadsheet to define the actual points
| bhh(n) total length of points |  | 0 | 108 | 8 | 54
Experimental Extensions | Reserved for experimental extensions | 30000
Vendor Points (VP) |  | 50000 | 50000 | 50000 | 50000 | 50000 |  | State if Storage
Start Index Points | Used for optional Auto Discovery | 60000 |  |  |  | 60000 |  | Yes | Storage? Yes or No
Maximum Index Value |  | 65535
mhbi(n) | Starting index of meter #n binary inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhbi(n) | Starting index of DER unit #n binary inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihbi(n) | Starting index of inverter #n binary inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhbi(n) | Starting index of battery #n binary inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhai(n) | Starting index of meter #n analog inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhai(n) | Starting index of DER unit #n analog inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihai(n) | Starting index of inverter #n analog inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhai(n) | Starting index of battery #n analog inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhao(n) | Starting index of meter #n analog outputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
ihao(n) | Starting index of inverter #n analog outputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhao(n) | Starting index of battery #n analog outputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)

## BO
DNP3 Point Index | Name / Description | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  |  |  | IEC61850UniqueString | Assoc. BI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BO3 | System Permission to Start | Start Permission Not Granted | Start Permission Granted | DGEN.PrmConn | BI16 | Enter Service | M | M
BO17 | Enable Active Power Limit Mode | Disable | Enable | DWMX.Mod | BI69 | Active Power Limit | C: For Function | M
BO25 | Enable Volt-Watt Mode | Disable | Enable | DVWC.Mod | BI77 | Volt-Watt | C: For Function | M
BO27 | Enable Constant Vars Mode | Disable | Enable | DVAR.Mod | BI79 | Const Vars | C: For Function | M
BO28 | Enable Constant Power Factor Mode | Disable | Enable | DFPF.Mod | BI80 | Constant PF | C: For Function | M
BO29 | Enable Volt-Var Control Mode | Disable | Enable | DVVR.Mod | BI81 | Volt-Var | C: For Function | M
BO41 | Volt-Var Enable Autonomous Voltage Reference Adjustment | Disable | Enable | DVVR.VRefAdjEna | BI93 | Volt-Var | C: For Function | M

## BI
DNP3 Point Index | Name / Description | Default Event Class | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Assoc. BO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BI0 | System Communication Error | 1 | Normal | Alarm: Communications error exists in the ESS | LCCH1.ChLiv |  | Alarm | M | M
BI1 | System Has Priority 1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH.GrAlm |  | Alarm | M | M
BI21 | DER is Off but Available to Start | 2 | Null | Off-Available | DGEN.DEROpSt.disconnectedandavailable |  | Monitoring | M | M
BI22 | DER is Off and Not Available to Start | 2 | Null | Off-Not-Available | DGEN.DEROpSt.disconnectedandblocked |  | Monitoring | M | M
BI31 | Supports Low/High Voltage Ride-Through Mode | 0 | Not Supported | Supported | DHVT |  | Volt Ride-Through | M | M
BI32 | Supports Low/High Frequency Ride-Through Mode | 0 | Not Supported | Supported | DHFT |  | Freq Ride-Through | M | M
BI35 | Supports Frequency-Watt Mode | 0 | Not Supported | Supported | DHFW |  | Freq-Watt | M | M
BI36 | Supports Active Power Limit Mode | 0 | Not Supported | Supported | DWMX |  | Active Power Limit | M | M
BI44 | Supports Volt-Watt Mode | 0 | Not Supported | Supported | DVWC |  | Volt-Watt | M | M
BI46 | Supports Constant VArs Mode | 0 | Not Supported | Supported | DVAR |  | Const Vars | M | M
BI47 | Supports Constant Power Factor Mode | 0 | Not Supported | Supported | DFPF |  | Constant PF | M | M
BI48 | Supports Volt-VAr Control Mode | 0 | Not Supported | Supported | DVVR |  | Volt-Var | M | M
BI49 | Supports Watt-VAr Mode | 0 | Not Supported | Supported | DWVR |  | Watt-Var | M | M
BI69 | Operating Mode - Active Power Limit Enabled | 2 | Disabled | Enabled | DWMX.Mod | BO17 | Active Power Limit | C: For Function | M
BI77 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWC.Mod | BO25 | Volt-Watt | C: For Function | M
BI79 | Operating Mode - Constant VArs Enabled | 2 | Disabled | Enabled | DVAR.Mod | BO27 | Const Vars | C: For Function | M
BI80 | Operating Mode - Constant Power Factor Enabled | 2 | Disabled | Enabled | DFPF.Mod | BO28 | Constant PF | C: For Function | M
BI81 | Operating Mode - Volt-VAR Control Enabled | 2 | Disabled | Enabled | DVVR.Mod | BO29 | Volt-Var | C: For Function | M
BI82 | Operating Mode - Watt-VAr Enabled | 2 | Disabled | Enabled | DWVR.Mod | BO30 | Watt-Var | C: For Function | M
BI5000 | Active Power at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotW.range |  | Equipment Data
BI5001 | Active Power at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotW.range |  | Equipment Data
BI5002 | Reactive Power at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotVAr.range |  | Equipment Data
BI5003 | Reactive Power at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotVAr.range |  | Equipment Data
BI5004 | Power Factor at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotPF.range |  | Equipment Data
BI5005 | Power Factor at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotPF.range |  | Equipment Data
BI5006 | Phase A Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsA.range |  | Equipment Data
BI5007 | Phase A Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsA.range |  | Equipment Data
BI5008 | Phase B Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsB.range |  | Equipment Data
BI5009 | Phase B Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsB.range |  | Equipment Data
BI5010 | Phase C Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsC.range |  | Equipment Data
BI5011 | Phase C Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsC.range |  | Equipment Data
BI5012 | Meter #1 Communication Error | 1 | Normal: No Active Communications Error | Alarm: Active Communications Error | Meter1.LCCH.ChLiv |  | Equipment Data
BI10000 | DER Unit #1 Is In Maintenance Operational State | 1 | Not in Maintenance | In Maintenance | DER_Unit1.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI10001 | DER Unit #1 Has P1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | DER_Unit1.CALH.GrAlm |  | Equipment Data
BI10002 | DER Unit #1 Has P2 Alarms | 1 | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | DER_Unit1.CALH.GrWrn |  | Equipment Data
BI10003 | DER Unit #1 Has P3 Alarms | 1 | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | DER_Unit1.CALH.GrInd |  | Equipment Data
BI15000 | Inverter #1 Active Power Output is Too High | 1 | Normal | Alarm | Inverter1.MMXU.TotW.range |  | Equipment Data
BI15001 | Inverter #1 Active Power Output is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.TotW.range |  | Equipment Data
BI15002 | Inverter #1 Reactive Power Output is Too High | 1 | Normal | Alarm | Inverter1.MMXU.TotVAr.range |  | Equipment Data
BI15003 | Inverter #1 Reactive Power Output is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.TotVAr.range |  | Equipment Data
BI15004 | Inverter #1 Current Output Frequency is Too High | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15005 | Inverter #1 Current Output Frequency is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15006 | Inverter #1 DC Input Power is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Watt.range |  | Equipment Data
BI15007 | Inverter #1 DC Input Power is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Watt.range |  | Equipment Data
BI15008 | Inverter #1 DC Current Level is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Amp.range |  | Equipment Data
BI15009 | Inverter #1 DC Current Level is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Amp.range |  | Equipment Data
BI15010 | Inverter #1 DC Input Voltage is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15011 | Inverter #1 DC Input Voltage is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15012 | Inverter #1 DNP3 Power Factor Excitation. Operating quadrant of the inverter. | 1 | Overexcited (producing VARs - Q1/Q2) | Underexcited (absorbing VARs - Q3/Q4) | Inverter1.DSTO.PFExtSet |  | Equipment Data
BI15013 | Inverter #1 Communication Error | 1 | Normal | Alarm | Inverter1.LCCH.ChLiv |  | Equipment Data
BI15014 | Inverter #1 Is In Local Control Mode | 1 | Normal | Alarm | Inverter1.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI15015 | Inverter #1 Is DC Contactor Closed | 1 | Normal | Alarm | Inverter1.DINV.InvSwiAlm |  | Equipment Data
BI15016 | Inverter #1 Ground Fault Alarm | 1 | Normal | Alarm | Inverter1.PDIS.Str |  | Equipment Data
BI15017 | Inverter #1 DC Over Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15018 | Inverter #1 DC Under Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15019 | Inverter #1 AC Disconnect Warning | 1 | Normal | Alarm | Inverter1.DINV.InvACLosAlm |  | Equipment Data
BI15020 | Inverter #1 DC Disconnect Warning | 1 | Normal | Alarm | Inverter1.DINV.InvDCLosAlm |  | Equipment Data
BI15021 | Inverter #1 Grid Disconnect Warning | 1 | Normal | Inverter does not detect power on the grid | Inverter1.DINV.InvGriLosAlm |  | Equipment Data
BI15022 | Inverter #1 Cabinet Open Warning | 1 | Normal | Alarm | Inverter1.SPSE.GteSt.open |  | Equipment Data
BI15023 | Inverter #1 Manual Shutdown Warning | 1 | Normal | Alarm | Inverter1.DINV.InvManStopSt |  | Equipment Data
BI15024 | Inverter #1 Over Temperature Alarm | 1 | Normal | Alarm | Inverter1.DINV.EnclTmp.range |  | Equipment Data
BI15025 | Inverter #1 Under Temperature Alarm | 1 | Normal | Alarm | Inverter1.DINV.EnclTmp.range |  | Equipment Data
BI15026 | Inverter #1 Over Frequency Alarm | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15027 | Inverter #1 Under Frequency Alarm | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15028 | Inverter #1 AC Over Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMXU.PhV.PhsA.range |  | Equipment Data
BI15029 | Inverter #1 AC Under Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMXU.PhV.PhsA.range |  | Equipment Data
BI15030 | Inverter #1 Blown String Fuse Alarm | 1 | Normal | Alarm | Inverter1.XFUS.FuSt |  | Equipment Data
BI15031 | Inverter #1 Memory Loss Alarm | 1 | Normal | Alarm | Inverter1.MESA.MemLosAlm |  | Equipment Data
BI15032 | Inverter #1 Hardware Test Failure | 1 | Normal | Alarm | Inverter1.DINV.TestRsl |  | Equipment Data
BI15033 | Inverter #1 Other Alarm | 1 | Normal | Alarm | Inverter1.CALH.GrAlm |  | Equipment Data
BI15034 | Inverter #1 Other Warning | 1 | Normal | Alarm | Inverter1.CALH.GrWrn |  | Equipment Data
BI20000 | Battery Bank #1 Status of Storage | 3 | Dis-connected | Connected | Battery1.DBAT.BatSt.connected |  | Equipment Data
BI20001 | Battery Bank #1 Communication Error | 1 | Normal | Alarm | Battery1.LCCH.ChLiv |  | Equipment Data
BI20002 | Battery Bank #1 Is In Local Control Mode | 1 | Not in Local Control | In Local Control | Battery1.DBAT.BatSt.localcontrol |  | Equipment Data
BI20003 | Battery Bank #1 Is DC Contactor Closed | 1 | Not Closed | Closed | Battery1.DBAT.DCSwCls |  | Equipment Data
BI20004 | Battery Bank #1 Is Charging | 1 | Not Charging | Charging | Battery1.DBAT.ChaSt |  | Equipment Data
BI20005 | Battery Bank #1 Is Discharging | 1 | Not Discharging | Discharging | Battery1.DBAT.DschSt |  | Equipment Data
BI20006 | Battery Bank #1 External Voltage is Too High | 1 | Normal | Alarm | Battery1.DBAT.ExtVolHiAlm |  | Equipment Data
BI20007 | Battery Bank #1 External Voltage is Too Low | 1 | Normal | Alarm | Battery1.DBAT.ExtVolLoAlm |  | Equipment Data
BI20008 | Battery Bank #1 Internal Voltage is Too High | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiAlm |  | Equipment Data
BI20009 | Battery Bank #1 Internal Voltage is Too Low | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoAlm |  | Equipment Data
BI20010 | Battery Bank #1 Over Temperature Alarm | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpHiAlm |  | Equipment Data
BI20011 | Battery Bank #1 Under Temperature Alarm | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpLoAlm |  | Equipment Data
BI20012 | Battery Bank #1 Temperature Imbalance Alarm | 1 | Normal | Alarm | Battery1.DBAT.UnbTmpAlm |  | Equipment Data
BI20013 | Battery Bank #1 Over Temperature Warning | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpHiWrn |  | Equipment Data
BI20014 | Battery Bank #1 Under Temperature Warning | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpLoWrn |  | Equipment Data
BI20015 | Battery Bank #1 Temperature Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbTmpWrn |  | Equipment Data
BI20016 | Battery Bank #1 Over Charge Current Alarm | 1 | Normal | Alarm | Battery1.DBAT.ChaAmpHiAlm |  | Equipment Data
BI20017 | Battery Bank #1 Over Discharge Current Alarm | 1 | Normal | Alarm | Battery1.DBAT.DschAmpHiAlm |  | Equipment Data
BI20018 | Battery Bank #1 Over Charge Current Warning | 1 | Normal | Alarm | Battery1.DBAT.ChaAmpHiWrn |  | Equipment Data
BI20019 | Battery Bank #1 Over Discharge Current Warning | 1 | Normal | Alarm | Battery1.DBAT.DschAmpHiWrn |  | Equipment Data
BI20020 | Battery Bank #1 Voltage Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbVolWrn |  | Equipment Data
BI20021 | Battery Bank #1 Current Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbAmpWrn |  | Equipment Data
BI20022 | Battery Bank #1 Over Voltage Alarm | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiAlm |  | Equipment Data
BI20023 | Battery Bank #1 Under Voltage Alarm | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoAlm |  | Equipment Data
BI20024 | Battery Bank #1 Over Voltage Warning | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiWrn |  | Equipment Data
BI20025 | Battery Bank #1 Under Voltage Warning | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoWrn |  | Equipment Data
BI20026 | Battery Bank #1 Over State of Charge Maximum Alarm | 1 | Normal | Alarm | Battery1.DBAT.SocHiAlm |  | Equipment Data
BI20027 | Battery Bank #1 Under State of Charge Minimum Alarm | 1 | Normal | Alarm | Battery1.DBAT.SocLoAlm |  | Equipment Data
BI20028 | Battery Bank #1 Over State of Charge Maximum Warning | 1 | Normal | Alarm | Battery1.DBAT.SocHiWrn |  | Equipment Data
BI20029 | Battery Bank #1 Under State of Charge Minimum Warning | 1 | Normal | Alarm | Battery1.DBAT.SocLoWrn |  | Equipment Data
BI20030 | Battery Bank #1 Contactor Failure | 1 | Normal | Alarm | Battery1.MESA.ContFail |  | Equipment Data
BI20031 | Battery Bank #1 Fan Error | 1 | Normal | Alarm | Battery1.MESA.FanErr |  | Equipment Data
BI20032 | Battery Bank #1 Ground Fault | 1 | Normal | Alarm | Battery1.MESA.GndFlt |  | Equipment Data
BI20033 | Battery Bank #1 Door Open Alarm | 1 | Normal | Alarm | Battery1.MESA.DoorOpnAlm |  | Equipment Data
BI20034 | Battery Bank #1 Configuration Error | 1 | Normal | Alarm | Battery1.MESA.ConfErr |  | Equipment Data
BI20035 | Battery Bank #1 Configuration Warning | 1 | Normal | Alarm | Battery1.MESA.ConfWrn |  | Equipment Data
BI20036 | Battery Bank #1 Other Alarm | 1 | Normal | Alarm | Battery1.MESA.OthAlm |  | Equipment Data
BI20037 | Battery Bank #1 Other Warning | 1 | Normal | Alarm | Battery1.MESA.OthWrn |  | Equipment Data
BI20038 | Battery Bank #1 Fire Alarm | 1 | Normal | Alarm | Battery1.SFIR.FireAlm |  | Equipment Data
BI20039 | Battery Bank #1 Fire Supervisory Warning | 1 | Normal | Alarm | Battery1.MESA.FireSupWrn |  | Equipment Data
BI20040 | Battery Bank #1 Fire Trouble Warning | 1 | Normal | Alarm | Battery1.MESA.FireWrn |  | Equipment Data
BI20041 | Battery Bank #1 Fire Power Fault Warning | 1 | Normal | Alarm | Battery1.MESA.FireFltWrn |  | Equipment Data
BI20042 | Battery Bank #1 Chiller Alarm | 1 | Normal | Alarm | Battery1.MESA.ClAlm |  | Equipment Data
BI20043 | Battery Bank #1 Chiller Warning | 1 | Normal | Alarm | Battery1.MESA.ClWrn |  | Equipment Data
BI20044 | Battery Bank #1 Air Handler Alarm | 1 | Normal | Alarm | Battery1.MESA.AirCtlAlm |  | Equipment Data
BI20045 | Battery Bank #1 Air Handler Warning | 1 | Normal | Alarm | Battery1.MESA.AirCtlWrn |  | Equipment Data
BI20046 | Battery Bank #1 Fluid Alarm | 1 | Normal | Alarm | Battery1.MESA.FluAlm |  | Equipment Data
BI20047 | Battery Bank #1 Fluid Warning | 1 | Normal | Alarm | Battery1.MESA.FluWrn |  | Equipment Data
BI20048 | Battery Bank #1 Gas Alarm | 1 | Normal | Alarm | Battery1.MESA.GasAlm |  | Equipment Data
BI20049 | Battery Bank #1 Gas Warning | 1 | Normal | Alarm | Battery1.MESA.GasWrn |  | Equipment Data
BI20050 | Battery Bank #1 Electrolyte Alarm | 1 | Normal | Alarm | Battery1.MESA.ElcytAlm |  | Equipment Data
BI20051 | Battery Bank #1 Electrolyte Warning | 1 | Normal | Alarm | Battery1.MESA.ElcytWrn |  | Equipment Data
BI20052 | Battery Bank #1 Electrical Alarm | 1 | Normal | Alarm | Battery1.MESA.ElcAlm |  | Equipment Data
BI20053 | Battery Bank #1 Electrical Warning | 1 | Normal | Alarm | Battery1.MESA.ElcWrn |  | Equipment Data

## AO
DNP3 Point Index | Name / Description | Transmitted Value |  | Scaling |  | Units | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  | Minimum | Maximum | Multiplier | OffSet |  | IEC61850UniqueString | Assoc. AI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AO23 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV1.BlkRef | AI73 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO24 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV1.BlkRef | AI74 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO25 | Low/High Voltage Ride-Through High Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV2.BlkRef | AI75 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO26 | Low/High Voltage Ride-Through Low Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV2.BlkRef | AI76 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO28 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF1.BlkRef | AI79 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO29 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF1.BlkRef | AI80 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO62 | Frequency-Watt High Starting Frequency | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | AI121 | Freq-Watt | C: For Function | M
AO64 | Frequency-Watt High Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | AI123 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO476 | M
AO66 | Frequency-Watt Low Starting Frequency | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | AI125 | Freq-Watt | C: For Function | M
AO68 | Frequency-Watt Low Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | AI127 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO477 | M
AO72 | Frequency-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.1 | AI131 | Freq-Watt |  | M
AO73 | Frequency-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | AI132 | Freq-Watt |  | M
AO87 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | AI148 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO478 | M
AO88 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | AI149 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO479 | M
AO173 | Volt-Watt Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVWC.VWCrv | AI248 | Volt-Watt | C: For Function, unless set at implementation as zero | C: See clause 1.7
AO175 | Volt-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.1 | AI251 | Volt-Watt | C: For Function | M
AO176 | Volt-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.2 | AI252 | Volt-Watt | C: For Function | M
AO203 | Constant Vars Reactive Power Target | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | AI281 | Const Vars | C: For Function | M
AO210 | Constant Power Factor Setpoint - Generation/Discharging | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | AI288 | Constant PF | C: For Function | M
AO211 | Constant Power Factor Setpoint - Charging | 0 | 100 | 0.01 | 0 | None | DFPF.PFLodTgt | AI289 | Constant PF | C: For Function | M
AO217 | Volt-Var Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVVR.VVArCrv | AI297 | Volt-Var | C: For Function | M
AO220 | Volt-Var Autonomous Voltage Reference Adjustment Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.VRefTmms | AI300 | Volt-Var | C: For Function | M
AO244 | Curve Edit Selector. Writing to this point selects which of the curves can currently be viewed and changed. | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | AI328 | Curve | C: See clause 1.7 | C: See clause 1.7
AO245 | Curve Type. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-Var <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | AI329 | Curve | C: See clause 1.7 | C: See clause 1.7
AO246 | Curve Number of Points | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | AI330 | Curve | C: See clause 1.7 | C: See clause 1.7
AO247 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time (milliseconds) <23> Celsius Temperature <29> Voltage (V) <33> Frequency (Hz) <38> Watts (W) <100> Price in hundredths of local currency <129> Percent Voltage <133> Percent Frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | AI331 | Curve | C: See clause 1.7 | C: See clause 1.7
AO248 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> Vars as percent of max Vars (VarMax) <3> Vars as percent of max available Vars (VarAval) <4> Vars as percent of max Watts (Wmax) - not used <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor <8> Volts as a percent of the nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage (V) <33> Frequency (Hz) <38> Watts (W) <99+> Other | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | AI332 | Curve | C: See clause 1.7 | C: See clause 1.7
AO249 | Curve Point 1 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | AI333 | Curve | C: See clause 1.7 | C: See clause 1.7
AO250 | Curve Point 1 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | AI334 | Curve | C: See clause 1.7 | C: See clause 1.7
AO251 | Curve Point 2 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | AI335 | Curve | C: See clause 1.7 | C: See clause 1.7
AO252 | Curve Point 2 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | AI336 | Curve | C: See clause 1.7 | C: See clause 1.7
AO253 | Curve Point 3 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | AI337 | Curve | C: See clause 1.7 | C: See clause 1.7
AO254 | Curve Point 3 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | AI338 | Curve | C: See clause 1.7 | C: See clause 1.7
AO255 | Curve Point 4 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | AI339 | Curve | C: See clause 1.7 | C: See clause 1.7
AO256 | Curve Point 4 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | AI340 | Curve | C: See clause 1.7 | C: See clause 1.7
AO480 | High Frequency-Watt Droop Upper Gradient | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | AI590 | Droop Freq-Watt | C: For Function | M
AO481 | Low Frequency-Watt Droop Lower Gradient | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | AI591 | Droop Freq-Watt | C: For Function | M
AO482 | High Frequency-Watt Droop Minimum Active Power | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | AI592 | Droop Freq-Watt | C: For Function | M
AO483 | Low Frequency-Watt Droop Maximum Active Power | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | AI593 | Droop Freq-Watt | C: For Function | M
AO509 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | AI619 | Active Power Limit | C: For Function if BI113 = 1 | M
AO510 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | AI620 | Active Power Limit | C: For Function if BI113 = 1 | M
AO511 | Constant Vars using vars as unit | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | AI621 | Constant Vars | C: For Function if BI115 = 1 | M
AO5000 | Meter #1 Active Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.hLim | AI5025 | Equipment Data
AO5001 | Meter #1 Active Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.lLim | AI5026 | Equipment Data
AO5002 | Meter #1 Reactive Power – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.hLim | AI5027 | Equipment Data
AO5003 | Meter #1 at Reactive Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.lLim | AI5028 | Equipment Data
AO5004 | Meter #1 at Power Factor – High Threshold | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.hLim | AI5029 | Equipment Data
AO5005 | Meter #1 at Power Factor – Low Threshold | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.lLim | AI5030 | Equipment Data
AO5006 | Meter #1 Phase A Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.hLim | AI5031 | Equipment Data
AO5007 | Meter #1 Phase A Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.lLim | AI5032 | Equipment Data
AO5008 | Meter #1 Phase B Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.hLim | AI5033 | Equipment Data
AO5009 | Meter #1 Phase B Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.lLim | AI5034 | Equipment Data
AO5010 | Meter #1 Phase C Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.hLim | AI5035 | Equipment Data
AO5011 | Meter #1 Phase C Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.lLim | AI5036 | Equipment Data
AO15000 | Inverter #1 Active Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.hLim | AI15021 | Equipment Data
AO15001 | Inverter #1 Active Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.lLim | AI15022 | Equipment Data
AO15002 | Inverter #1 Reactive Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.hLim | AI15023 | Equipment Data
AO15003 | Inverter #1 Reactive Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.lLim | AI15024 | Equipment Data
AO15004 | Inverter #1 Current Output Frequency – High Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.hLim | AI15025 | Equipment Data
AO15005 | Inverter #1 Current Output Frequency – Low Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.lLim | AI15026 | Equipment Data
AO15006 | Inverter #1 DC Inverter Input Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.hLim | AI15027 | Equipment Data
AO15007 | Inverter #1 DC Inverter Input Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.lLim | AI15028 | Equipment Data
AO15008 | Inverter #1 DC Current Available – High Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter1.MMDC.Amp.RangeC.hLim | AI15029 | Equipment Data
AO15009 | Inverter #1 DC Current Available – Low Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter1.MMDC.Amp.RangeC.lLim | AI15030 | Equipment Data
AO15010 | Inverter #1 DC Voltage Between DER System and Inverter – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.hLim | AI15031 | Equipment Data
AO15011 | Inverter #1 DC Voltage Between DER System and Inverter – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.lLim | AI15032 | Equipment Data
AO20000 | Battery Bank #1 External Voltage - High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolHiAls | AI20023 | Equipment Data
AO20001 | Battery Bank #1 External Voltage - Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolLoAls | AI20024 | Equipment Data
AO20002 | Battery Bank #1 Internal Voltage – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolHiAls | AI20025 | Equipment Data
AO20003 | Battery Bank #1 Internal Voltage – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolLoAls | AI20026 | Equipment Data

## AI
DNP3 Point Index | Name / Description | Default Event Class | Transmitted Value |  | Scaling |  | Units | IEC61850 | Additional Information |  |  |  |  | EUT Capabilities
|  |  | Minimum | Maximum | Multiplier | Offset |  | IEC61850UniqueString | Value | Assoc. AO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AI2 | Nameplate Minimum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMinRtg | 0 |  | Nameplate | M | M
AI3 | Nameplate Maximum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMaxRtg | 0 |  | Nameplate | M | M
AI4 | Nameplate Active Generation Power Rating at Unity Power Factor | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMaxRtg | 0 |  | Nameplate | M | M
AI6 | Nameplate Active Generation Power Rating at Specified Over-Excited Power Factor, injecting reactive power (as positive vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WOvPFRtg | 0 |  | Nameplate | M | M
AI8 | Specified Over-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.OvPFRtg | 0 |  | Nameplate | M | M
AI9 | Nameplate Active Generation Power Rating at Specified Under-Excited Power Factor, absorbing reactive power (as negative vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WUnPFRtg | 0 |  | Nameplate | M | M
AI10 | Nameplate Active Charging Power Rating at Specified Under-Excited Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWUnPFRtg | 0 |  | Nameplate | M | M
AI11 | Specified Under-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.UnPFRtg | 0 |  | Nameplate | M | M
AI12 | Nameplate Reactive Supply (Injection) Power Rating | 3 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMaxRtg | 0 |  | Nameplate | M | M
AI13 | Nameplate Reactive Absorption Power Rating | 3 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMaxRtg | 0 |  | Nameplate | M | M
AI15 | Nameplate Apparent Charging Power Rating | 3 | -2147483648 | 0 | 1 | 0 | VAs | DSTO.ChaVAMaxRtg | 0 |  | Nameplate | M | M
AI16 | Nameplate Storage Actual Energy Capacity. Nameplate (original) actual total energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.WhRtg | 0 |  | Nameplate | C: For Storage | M
AI21 | Remaining Reactive Susceptance | 3 | -2147483648 | 2147483647 | 1 | 0 | Siemens | DGEN.SuscRtg | 0 |  | Nameplate |  | M
AI22 | IEEE 1547 Normal Operating Performance Category. Enumeration: <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DGEN.RegClas.1 | 0 |  | Nameplate | M | M
AI23 | IEEE 1547 Abnormal Operating Performance Category. Enumeration: <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DGEN.RegClas.2 | 0 |  | Nameplate | M | M
AI29 | Reference Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VRef | 0 | AO0 | Config | M | M
AI30 | Reference Voltage Offset | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts | DECP.VRefOfs | 0 | AO1 | Config | M | M
AI32 | Maximum Active Generation Power | 2 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMax | 0 |  | Operational Settings | M | M
AI34 | Maximum Reactive Injection Power | 2 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMax | 0 |  | Operational Settings | M | M
AI35 | Maximum Reactive Absorption Power | 2 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMax | 0 |  | Operational Settings | M | M
AI48 | System Usable State of Charge. Present usable energy in the DER as a percentage of Nameplate Storage Usable Capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DSTO.UseSocPct | 0 |  | Monitoring | C: For Storage | M
AI121 | Frequency-Watt High Starting Frequency. Delta frequency between start frequency and nominal grid frequency for High frequency events. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | 0 | AO62 | Freq-Watt | C: For Function | M
AI123 | Frequency-Watt High Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | 0 | AO64 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI586 | M
AI125 | Frequency-Watt Low Starting Frequency. Delta frequency between start frequency and nominal grid frequency for low frequency events. | 2 | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | 0 | AO66 | Freq-Watt | C: For Function | M
AI127 | Frequency-Watt Low Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | 0 | AO68 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI587 | M
AI131 | Frequency-Watt Ramp Up Time Constant. Time constant or open loop response time for moving from the current active power target to a Higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DLFW1.OplTmsMax.1 | 0 | AO72 | Freq-Watt | C: For Function | M
AI132 | Frequency-Watt Ramp Down Time Constant. Time constant or open loop response time for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | 0 | AO73 | Freq-Watt |  | M
AI148 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | 0 | AO87 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI588 | M
AI149 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | 0 | AO88 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI589 | M
AI246 | Volt-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | 0 | AO172 | Volt-Watt | C: For Function | M
AI247 | Volt-Watt Reference Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.MMXN.Vol | 0 |  | Volt-Watt | C: For Function | M
AI248 | Volt-Watt Curve Index. Index of the Volt-Watt curve that should be used by the mode. If zero, then direct paramters are used. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | 0 | AO173 | Volt-Watt | C: For Function | M
AI281 | Constant VArs Reactive Power Target. Percentage of maximum reactive power. | 2 | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | 0 | AO203 | Const VArs | C: For Function | M
AI288 | Constant Power Factor Setpoint - Generation / Discharging | 2 | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | 0 | AO210 | Constant PF | C: For Function | M
AI328 | Curve Edit Selector | 2 | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | 1 | AO244 | Curve | M | C: See clause 1.7
AI329 | Curve Type. Enumeration: <0> Curve disabled <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-VAr <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 2 | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | 0 | AO245 | Curve | M | C: See clause 1.7
AI330 | Curve Number of Points | 2 | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | 0 | AO246 | Curve | M | C: See clause 1.7
AI331 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time <29> Voltage <33> Frequency <38> Watts <23> Celsius Temperature <100> Price in hundredths of local currency <129> Voltage as a percent of nominal voltage (VRef) <133> Frequency as a percent of nominal frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | 0 | AO247 | Curve | M | C: See clause 1.7
AI332 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> VArs as percent of max VArs (VARMax) <3> VArs as percent of max available VArs (VArAval) <4> Vars as percent of max apparent Watts (VAMax) - used in IEEE 1547 <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor in EEI notation <8> Volts as a percent of nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage <33> Frequency <38> Watts <99+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | 0 | AO248 | Curve | M | C: See clause 1.7
AI333 | Curve Point 1 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | 0 | AO249 | Curve | M | C: See clause 1.7
AI334 | Curve Point 1 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | 0 | AO250 | Curve | M | C: See clause 1.7
AI335 | Curve Point 2 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | 0 | AO251 | Curve | M | C: See clause 1.7
AI336 | Curve Point 2 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | 0 | AO252 | Curve | M | C: See clause 1.7
AI337 | Curve Point 3 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | 0 | AO253 | Curve | M | C: See clause 1.7
AI338 | Curve Point 3 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | 0 | AO254 | Curve | M | C: See clause 1.7
AI339 | Curve Point 4 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | 0 | AO255 | Curve | M | C: See clause 1.7
AI340 | Curve Point 4 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | 0 | AO256 | Curve | M | C: See clause 1.7
AI536 | System Meter Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | SYS.MMXU.Hz | 0 |  | Monitoring | M | M
AI537 | System Meter Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW | 0 |  | Monitoring | M | M
AI541 | System Meter Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | SYS.MMXU.TotVAr | 0 |  | Monitoring | M | M
AI547 | System Meter Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.mag | 0 |  | Monitoring | M | M
AI548 | System Meter Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsA.ang | 0 |  | Monitoring | M | M
AI549 | System Meter Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.mag | 0 |  | Monitoring | M | M
AI550 | System Meter Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsB.ang | 0 |  | Monitoring | M | M
AI551 | System Meter Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.mag | 0 |  | Monitoring | M | M
AI552 | System Meter Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsC.ang | 0 |  | Monitoring | M | M
AI553 | System Meter Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.AvPPVPhs | 0 |  | Monitoring | M | M
AI554 | System Meter Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsA.mag | 0 |  | Monitoring | M | M
AI555 | System Meter Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsB.mag | 0 |  | Monitoring | M | M
AI556 | System Meter Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsC.mag | 0 |  | Monitoring | M | M
AI590 | Frequency-Watt Droop High Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | 0 | AO480 | Droop Freq-Watt | C: For Function | M
AI591 | Frequency-Watt Droop Low Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | 0 | AO481 | Droop Freq-Watt | C: For Function | M
AI592 | High Frequency-Watt Droop Minimum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | 0 | AO482 | Droop Freq-Watt | C: For Function | M
AI593 | Low Frequency-Watt Droop Maximum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | 0 | AO483 | Droop Freq-Watt | C: For Function | M
AI619 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | 0 | AO509 | Active Power Limit | C: For Function if BI113 = 1 | M
AI620 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | 0 | AO510 | Active Power Limit | C: For Function if BI113 = 1 | M
AI621 | Constant Vars using vars as unit | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | 0 | AO511 | Constant Vars | C: For Function if BI115 = 1 | M
AI5000 | Meter #1 Type of Connection Point | 3 | 0 | 99 | 1 | 0 | Enum | Meter1.DECP.EcpConnType | 0 |  | Equipment Data
AI5001 | Meter #1 DER Input/Output Included. <0> unknown <1> metered value does not include input/output of the DER <2> metered value includes all input/output of the DER <3> other | 3 | 0 | 3 | 1 | 0 | Enum | Meter1.DECP.DERMsIncl | 0 |  | Equipment Data
AI5002 | Meter #1 Type of Circuit Phases. <0> unknown <1> Single phase <2> Split phase <3> 2-phase <4> 3-phase delta <5> 3-phase wye <6> 3-phase wye grounded <7> 3-phase / 3-wire (inverter type) <8> 3-phase / 4-wire (inverter type) | 3 | 0 | 8 | 1 | 0 | Enum | Meter1.DECP.PhsConnTyp | 0 |  | Equipment Data
AI5003 | Meter #1 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Meter1.MMXU.ClcTotVA | 0 |  | Equipment Data
AI5004 | Meter #1 Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | Meter1.MMXU.Hz | 0 |  | Equipment Data
AI5005 | Meter #1 Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW | 0 |  | Equipment Data
AI5006 | Meter #1 Active Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsA.mag | 0 |  | Equipment Data
AI5007 | Meter #1 Active Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsB.mag | 0 |  | Equipment Data
AI5008 | Meter #1 Active Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsC.mag | 0 |  | Equipment Data
AI5009 | Meter #1 Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr | 0 |  | Equipment Data
AI5010 | Meter #1 Reactive Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsA.mag | 0 |  | Equipment Data
AI5011 | Meter #1 Reactive Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsB.mag | 0 |  | Equipment Data
AI5012 | Meter #1 Reactive Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsC.mag | 0 |  | Equipment Data
AI5013 | Meter #1 Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF | 0 |  | Equipment Data
AI5014 | Meter #1 Apparent Power | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | Meter1.MMXU.TotVA | 0 |  | Equipment Data
AI5015 | Meter #1 Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.mag | 0 |  | Equipment Data
AI5016 | Meter #1 Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsA.ang | 0 |  | Equipment Data
AI5017 | Meter #1 Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.mag | 0 |  | Equipment Data
AI5018 | Meter #1 Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsB.ang | 0 |  | Equipment Data
AI5019 | Meter #1 Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.mag | 0 |  | Equipment Data
AI5020 | Meter #1 Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsC.ang | 0 |  | Equipment Data
AI5021 | Meter #1 Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.AvPPVPhs | 0 |  | Equipment Data
AI5022 | Meter #1 Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsA.mag | 0 |  | Equipment Data
AI5023 | Meter #1 Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsB.mag | 0 |  | Equipment Data
AI5024 | Meter #1 Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsC.mag | 0 |  | Equipment Data
AI5025 | Meter #1 Active Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.hLim | 0 | AO5000 | Equipment Data
AI5026 | Meter #1 Active Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.lLim | 0 | AO5001 | Equipment Data
AI5027 | Meter #1 Reactive Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.hLim | 0 | AO5002 | Equipment Data
AI5028 | Meter #1 Reactive Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.lLim | 0 | AO5003 | Equipment Data
AI5029 | Meter #1 Power Factor – High Threshold | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.hLim | 0 | AO5004 | Equipment Data
AI5030 | Meter #1 Power Factor – Low Threshold | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.lLim | 0 | AO5005 | Equipment Data
AI5031 | Meter #1 Phase A Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.hLim | 0 | AO5006 | Equipment Data
AI5032 | Meter #1 Phase A Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.lLim | 0 | AO5007 | Equipment Data
AI5033 | Meter #1 Phase B Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.hLim | 0 | AO5008 | Equipment Data
AI5034 | Meter #1 Phase B Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.lLim | 0 | AO5009 | Equipment Data
AI5035 | Meter #1 Phase C Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.hLim | 0 | AO5010 | Equipment Data
AI5036 | Meter #1 Phase C Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.lLim | 0 | AO5011 | Equipment Data
AI10000 | DER Unit #1 Unit Type. Enumeration: <0> unknown <1> Diesel / gas engine <2> Gas Turbine engine <3> PV <4> PV plus Storage <5> Lithium Ion Battery Storage <6> Fuel cell <7> Hydro generator <8> Wind turbine <9> Flow battery storage <10> Air compression storage <11> Flywheel storage <12> Capacitor storage <13> Vehicle-to-Grid (V2G) <50> Mixed, hybrid DER <98> Not applicable / Unknown <99> Other | 3 | 0 | 99 | 1 | 0 | Enum | DER_Unit1.DGEN.DERTyp | 0 |  | Equipment Data
AI10001 | DER Unit #1 Nameplate Energy Capacity. Nameplate energy capacity for the DER unit expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DER_Unit1.DGEN.WMeteraxRtg | 0 |  | Equipment Data
AI10002 | IEEE 1547 Normal Operating Performance Category. <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DER_Unit1.DGEN.RegCls.1 | 0 |  | Equipment Data
AI10003 | IEEE 1547 Abnormal Operating Performance Category. <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DER_Unit1.DGEN.RegCls.2 | 0 |  | Equipment Data
AI10004 | DER Unit #1 Maximum Apparent Generation Power | 2 | 0 | 2147483647 | 1 | 0 | VA | DER_Unit1.DGEN.VAMax | 0 |  | Equipment Data
AI10005 | DER Unit #1 Maximum Apparent Charging Power | 2 | -2147483648 | 0 | 1 | 0 | VA | DER_Unit1.DSTO.ChaVAMax | 0 |  | Equipment Data
AI10006 | DER Unit #1 Operational Time. Time in seconds since commissioning. | 3 | 0 | 2147483647 | 1 | 0 | Seconds | DER_Unit1.DGEN.GnOpTms | 0 |  | Equipment Data
AI10007 | DER Unit #1 Connection Time. Number of hours the DER unit has been connected to the power system. | 3 | 0 | 2147483647 | 1 | 0 | Hours | DER_Unit1.DGEN.OpTmRs | 0 |  | Equipment Data
AI10008 | DER Unit #1 Available Active Generation Power | 1 | 0 | 2147483647 | 1 | 0 | W | DER_Unit1.DSTO.WAvlUp | 0 |  | Equipment Data
AI10009 | DER Unit #1 Available Active Charging Power | 1 | -2147483648 | 0 | 1 | 0 | W | DER_Unit1.DSTO.WAvlDn | 0 |  | Equipment Data
AI10010 | DER Unit #1 Available Reactive Injection Power | 1 | 0 | 2147483647 | 1 | 0 | Vars | DER_Unit1.DGEN.TotIvarAvl | 0 |  | Equipment Data
AI10011 | DER Unit #1 Available Reactive Absorption Power | 1 | -2147483648 | 0 | 1 | 0 | Vars | DER_Unit1.DGEN.TotAvarAvl | 0 |  | Equipment Data
AI10012 | DER Unit #1 Non-impacting Injection VArs Available. VArs that can be injected without impacting Active Power Output | 2 | 0 | 2147483647 | 1 | 0 | Vars | DER_Unit1.DGEN.IvarAvl | 0 |  | Equipment Data
AI10013 | DER Unit #1 Non-impacting Absorption VArs Available. VArs that can be absorbed without impacting Active Power Output | 2 | -2147483648 | 0 | 1 | 0 | Vars | DER_Unit1.DGEN.AvarAvl | 0 |  | Equipment Data
AI10014 | DER Unit #1 Link to Meter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | DER_Unit1.MESA.MeterNum | 0 |  | Equipment Data
AI15000 | Inverter #1 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Inverter1.MMXU.ClcTotVA | 0 |  | Equipment Data
AI15001 | Inverter #1 Active Power Target | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter1.DINV.WTgt | 0 |  | Equipment Data
AI15002 | Inverter #1 Reactive Power Target | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter1.DINV.VArTgtPct | 0 |  | Equipment Data
AI15003 | Inverter #1 Active Power. Present active power measurement. | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW | 0 |  | Equipment Data
AI15004 | Inverter #1 Reactive Power. Present reactive power measurement. | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr | 0 |  | Equipment Data
AI15005 | Inverter #1 Power Factor | 2 | -100 | 100 | 0.01 | 0 | None | Inverter1.MMXU.TotPF | 0 |  | Equipment Data
AI15006 | Inverter #1 Apparent Power | 2 | -2147483648 | 2147483647 | 1 | 0 | VA | Inverter1.MMXU.TotVA | 0 |  | Equipment Data
AI15007 | Inverter #1 DC Input Power | 3 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt | 0 |  | Equipment Data
AI15008 | Inverter #1 DC Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol | 0 |  | Equipment Data
AI15009 | Inverter #1 DC Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp | 0 |  | Equipment Data
AI15010 | Inverter #1 Average Line to Neutral Voltage. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PhV | 0 |  | Equipment Data
AI15011 | Inverter #1 Voltage Phase A to B. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsAB | 0 |  | Equipment Data
AI15012 | Inverter #1 Voltage Phase B to C. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsBC | 0 |  | Equipment Data
AI15013 | Inverter #1 Voltage Phase C to A. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsCA | 0 |  | Equipment Data
AI15014 | Inverter #1 AC Current. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A | 0 |  | Equipment Data
AI15015 | Inverter #1 Current Phase A. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsA | 0 |  | Equipment Data
AI15016 | Inverter #1 Current Phase B. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsB | 0 |  | Equipment Data
AI15017 | Inverter #1 Current Phase C. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsC | 0 |  | Equipment Data
AI15018 | Inverter #1 Internal (Cabinet) Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.EnclTmp | 0 |  | Equipment Data
AI15019 | Inverter #1 Heat Sink Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.HeatSinkTmp | 0 |  | Equipment Data
AI15020 | Inverter #1 Transformer Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.TrfTmp | 0 |  | Equipment Data
AI15021 | Inverter #1 Active Power Output - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.hLim | 0 | AO15000 | Equipment Data
AI15022 | Inverter #1 Active Power Output - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.lLim | 0 | AO15001 | Equipment Data
AI15023 | Inverter #1 Reactive Power Output – High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.hLim | 0 | AO15002 | Equipment Data
AI15024 | Inverter #1 Reactive Power Output – Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.lLim | 0 | AO15003 | Equipment Data
AI15025 | Inverter #1 Current Output Frequency – High Threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.hLim | 0 | AO15004 | Equipment Data
AI15026 | Inverter #1 Current Output Frequency – Low Threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.lLim | 0 | AO15005 | Equipment Data
AI15027 | Inverter #1 DC Inverter Input Power - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.hLim | 0 | AO15006 | Equipment Data
AI15028 | Inverter #1 DC Inverter Input Power - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.lLim | 0 | AO15007 | Equipment Data
AI15029 | Inverter #1 DC Current Available – High Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp.RangeC.hLim | 0 | AO15008 | Equipment Data
AI15030 | Inverter #1 DC Current Available – Low Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp.RangeC.lLim | 0 | AO15009 | Equipment Data
AI15031 | Inverter #1 DC Voltage Between DER System and Inverter – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.hLim | 0 | AO15010 | Equipment Data
AI15032 | Inverter #1 DC Voltage Between DER System and Inverter – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.lLim | 0 | AO15011 | Equipment Data
AI15033 | Inverter #1 Link to DER Unit # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Inverter1.MESA.DER_UnitNum | 0 |  | Equipment Data
AI20000 | Battery Bank #1 Type of Storage. <0> n/a, Unknown <1> Lead-acid <2> Nickel-metal hydrate (NiMH) <3> Nickel-cadmium (NiCad) <4> LitInverterum <5> Carbon zinc <6> Zinc chloride <7> Alkaline <8> Rechargeable alkaline <9> Sodium sulphur (NaS) <10> Flow <99> Other | 2 | 0 | 99 | 1 | 0 | Enum | Battery1.DBAT.BatTyp | 0 |  | Equipment Data
AI20001 | Battery Bank #1 Nameplate Actual Capacity Rating. The actual total capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery1.DBAT.WMeteraxRtg | 0 |  | Equipment Data
AI20002 | Battery Bank #1 Effective Capacity. The present effective capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery1.DBAT.EffWh | 0 |  | Equipment Data
AI20003 | Battery Bank #1 Minimum Reserve for Storage. As a percentage of the nominal useable storage (DBAT.CapWhUseRtg) | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.UseWMeterinPct | 0 |  | Equipment Data
AI20004 | Battery Bank #1 Maximum Reserve for Storage. As a percentage of the nominal useable storage (DBAT.CapWhUseRtg). Expressed as a delta from the maximum usable capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.UseWMeteraxPct | 0 |  | Equipment Data
AI20005 | Battery Bank #1 Battery State. <0> n/a, Unknown <1> Disconnected <2> Initializing <3> Connected <4> Standby <5> SOC Protection <6> Suspending <99> Fault | 2 | 0 | 99 | 1 | 0 | Enum | Battery1.DBAT.BatSt | 0 |  | Equipment Data
AI20006 | Battery Bank #1 Actual State of Charge. Currently available energy in the battery, as a percentage of the effective capacity. | 3 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.SocWh | 0 |  | Equipment Data
AI20007 | Battery Bank #1 State of Health. The ratio (expressed as a percentage) of the current rating of the battery with respect to the nameplate rating of the battery and end-of-life criteria. The rating of the battery may include one or more battery parameters that are selected as appropriate for the application and implementation. These parameters often include the energy capacity, but could also incorporate other measurements. | 1 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.EffWhPct | 0 |  | Equipment Data
AI20008 | Battery Bank #1 External Battery Voltage. Voltage measured between battery charger and battery. | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVol | 0 |  | Equipment Data
AI20009 | Battery Bank #1 Internal Battery Voltage. Internal voltage measurement. | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVol | 0 |  | Equipment Data
AI20010 | Battery Bank #1 Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Battery1.DBAT.Amp | 0 |  | Equipment Data
AI20011 | Battery Bank #1 Power | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Watts | Battery1.DBAT.Watt | 0 |  | Equipment Data
AI20012 | Battery Bank #1 Minimum Cell Voltage. Minimum cell voltage measurement of all cells in the bank. | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery1.SBAT.CelVolLo | 0 |  | Equipment Data
AI20013 | Battery Bank #1 Maximum Cell Voltage. Maximum cell voltage measurement of all cells in the bank. | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery1.SBAT.CelVolInverter | 0 |  | Equipment Data
AI20014 | Battery Bank #1 Minimum Temperature. Minimum temperature measurement for all sensors in the bank. | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.SBAT.CelTmpMin | 0 |  | Equipment Data
AI20015 | Battery Bank #1 Maximum Temperature. Maximum temperature measurement for all sensors in the bank. | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.SBAT.CelTmpMax | 0 |  | Equipment Data
AI20016 | Battery Bank #1 External Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.DBAT.ExtTmp | 0 |  | Equipment Data
AI20017 | Battery Bank #1 Internal Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.DBAT.IntnTmp | 0 |  | Equipment Data
AI20018 | Battery Bank #1 Charge Current Limit. Instantaneous current limit on charging. | 1 | -2147483648 | 0 | 0.1 | 0 | Amps | Battery1.DBAT.ChaAmpLim | 0 |  | Equipment Data
AI20019 | Battery Bank #1 Discharge Current Limit. Instantaneous current limit on discharging. | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | Battery1.DBAT.DschAmpLim | 0 |  | Equipment Data
AI20020 | Battery Bank #1 Minimum Voltage Limit. Instantaneous minimum voltage limit. | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.VolMinLim | 0 |  | Equipment Data
AI20021 | Battery Bank #1 Maximum Voltage Limit. Instantaneous maximum voltage limit. | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.VolMaxLim | 0 |  | Equipment Data
AI20022 | Battery Bank #1 Connected String Count. Number of strings in the bank that are currently connected. | 1 | 0 | 2147483647 | 1 | 0 | n/a | Battery1.DBAT.CelStrgCnt | 0 |  | Equipment Data
AI20023 | Battery Bank #1 External Voltage - High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolInverterAls | 0 | AO20000 | Equipment Data
AI20024 | Battery Bank #1 External Voltage - Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolLoAls | 0 | AO20001 | Equipment Data
AI20025 | Battery Bank #1 Internal Voltage – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolInverterAls | 0 | AO20002 | Equipment Data
AI20026 | Battery Bank #1 Internal Voltage – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolLoAls | 0 | AO20003 | Equipment Data
AI20027 | Battery Bank #1 Link to Inverter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Battery1.MESA.InverterNum | 0 |  | Equipment Data

## CTR
DNP3 Point Index | Name / Description | Default Class Assigned to Counter Events | Frozen Counter Exists (Yes or No) | Default Class Assigned to Frozen Counter Events | IEC 61850 | Additional Information |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Purpose/Mode/ Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
CTR5000 | Meter #1 Active Energy Delivered. Measured in watt-hours. | n/a | Yes | 3 | HM1MMTR.SupWh | Metering
CTR5001 | Meter #1 Active Energy Received. Measured in watt-hours. | n/a | Yes | 3 | HM1MMTR.DmdWh | Metering
CTR5002 | Meter #1 Reactive Energy Delivered. Measured in VAr-hours. | n/a | Yes | 3 | HM1MMTR.SupVArh | Metering
CTR5003 | Meter #1 Reactive Energy Received. Measured in VAr-hours. | n/a | Yes | 3 | HM1MMTR.DmdVArh | Metering

## System Diagrams
Naming of Data Objects