## Key
IEEE 1815.2 Standard Profile Companion Data Point Tables: Version 1.1
DNP3 Points |  | Start Index | BO | BI | AO | AI | CTR
SCADA
Configuration & Control Points |  | 0 | 0 | 0 | 0 | 0 | 0
Functions |  | 0 | 12 | 31 | 22 | 71 | 0 |  | Configuration Settings
Curves | Max of 100 x,y pairs per Curve | 0 | 0 | 107 | 244 | 328 | 0 |  | Allocate the number of curves and the maximum number of points per curve
System Meter |  | 0 | 0 | 94 | 449 | 533 | 0
Extensions beyond DNP3 AN2018-001 |  | 0 | 42 | 108 | 461 | 569 | 0
Gap #1 | Reserved for future extensions | x | 44 | 111 | 476 | 586
Schedules
Schedules (2 items/step) | Time offset, value (for backwards compat) | 2000 | 2000 | 2000 | 2000 | 2000 |  |  | Allocate number of schedules and the maximum points per schedule
Schedule Status (2 items) | Schedule Status of first 100 | 2300 |  | 2300 |  | 2300
Schedules (4 items/step) | Time offset, Action type, AO or BO Index, & Value | 3000 | 3000 | 3000 | 3000 | 3000
Schedule Status (4 items) | Schedule Status of first 100 | 3500 | - | 3500 | - | 3500
Gap #2 | Reserved for future extensions | 4000
Equipment Points |  |  | BO | BI | AO | AI | CTR | Enter Maximum # of Devices
Meters | Start of additional meter points | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 1 | No. of Meters
| mh(1) set of points per meter |  | 0 | 13 | 12 | 37 | 4
| mh(n) total length of points |  | 0 | 39 | 36 | 111 | 12
DER Units | Start of DER unit points. | 10000 | 10000 | 10000 | 10000 | 10000 |  | 1 | No. DER Units
| duh(1) set of points per DER unit |  | 0 | 4 | 0 | 15 | 0
| duh(n) total length of points |  | 0 | 28 | 0 | 98
Inverters | Start of inverter points. | 15000 | 15000 | 15000 | 15000 | 15000 |  | 1 | No. Inverters
| ihh(1) set of points per inverter |  | 0 | 35 | 12 | 34 | 0
| ihh(n) total length of points |  | 0 | 70 | 24 | 66
Batteries | Start of battery points. | 20000 | 20000 | 20000 | 20000 | 20000 |  | 1 | No. Batteries
| bhh(1) set of points per battery |  | 0 | 54 | 4 | 28 | 0 | For each meter, DER unit, inverter, and battery, additional historical data rows need to be added in the spreadsheet to define the actual points
| bhh(n) total length of points |  | 0 | 108 | 8 | 54
Experimental Extensions | Reserved for experimental extensions | 30000
Vendor Points (VP) |  | 50000 | 50000 | 50000 | 50000 | 50000 |  | State if Storage
Start Index Points | Used for optional Auto Discovery | 60000 |  |  |  | 60000 |  | Yes | Storage? Yes or No
Maximum Index Value |  | 65535
mhbi(n) | Starting index of meter #n binary inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhbi(n) | Starting index of DER unit #n binary inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihbi(n) | Starting index of inverter #n binary inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhbi(n) | Starting index of battery #n binary inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhai(n) | Starting index of meter #n analog inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhai(n) | Starting index of DER unit #n analog inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihai(n) | Starting index of inverter #n analog inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhai(n) | Starting index of battery #n analog inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhao(n) | Starting index of meter #n analog outputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
ihao(n) | Starting index of inverter #n analog outputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhao(n) | Starting index of battery #n analog outputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)

## BO
DNP3 Point Index | Name / Description | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  |  |  | IEC61850UniqueString | Assoc. BI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BO0 | System Set Lockout State | Not Locked Out | Lock Out | DSTO.DEROpSt.disconnectedandblocked | BI11 | State | M
BO1 | System Initiate Start-up Sequence (Return to Service) | No Change | Initiate Start-up | DCTE.CeaEgzReqCtl.2 | BI12 | State | M
BO2 | System Execute Stop (Cease to Energize) | No Change | Stop (Emergency) | DCTE.CeaEgzReqCtl.1 | BI15 | State | M
BO3 | System Permission to Start | Start Permission Not Granted | Start Permission Granted | DGEN.PrmConn | BI16 | Enter Service | M | M
BO6 | Islanded Mode. Determines how the DER behaves when in an Islanded configuration. <0> Isochronous Mode. DER attempts to control voltage and frequency independent of configured curves and settings up to the limits of the machine's capabilities in order to achieve AO reference voltage and AO nominal frequency. <1> Droop Mode. DER acts as a follower using Volt/Var and Freq/Watt curves. | Isochronous Mode | Droop Mode | DGEN.IsldCtlFol | BI25 | State | C: If in microgrid configuration
BO7 | Enable Sensed Grid Config Detection. If Enabled, the DER may independently change its Active Settings Group based on locally observed grid conditions. <0> No Autonomous Detection. <1> Autonomous Detection. Inverter's Active Settings Group may differ from the Requested Settings Group | No Autonomous Detection | Autonomous Detection | DECP.ECPIsldAuto | BI26 | State | C: If in microgrid configuration
BO12 | Enable Low/High Voltage Ride-Through Mode | Disable | Enable | DHVT.Mod | BI64 | Volt Ride-Through | C: For Function
BO13 | Enable Low/High Frequency Ride-Through Mode | Disable | Enable | DHFT.Mod | BI65 | Freq Ride-Through | C: For Function
BO14 | Enable Dynamic Reactive Current Support Mode | Disable | Enable | DRGS.Mod | BI66 | Dyn React Curr Supp | C: For Function
BO15 | Enable Dynamic Volt-Watt Mode | Disable | Enable | DVWD.Mod | BI67 | Dyn Volt-Watt | C: For Function
BO16 | Enable Frequency-Watt Droop Mode | Disable | Enable | DHFW1.Mod | BI68 | Freq-Watt | C: For Function
BO17 | Enable Active Power Limit Mode | Disable | Enable | DWMX.Mod | BI69 | Active Power Limit | C: For Function | M
BO18 | Enable Charge/Discharge Mode | Disable | Enable | DWGC.Mod | BI70 | Set Active Power | C: For Function
BO19 | Enable Coordinated Charge/Discharge Mode | Disable | Enable | DTCD.Mod | BI71 | Coord Charge-Dischg | C: For Function
BO20 | Enable Active Power Following Mode #1 (Peak Power Limiting) | Disable | Enable | DWFL1.Mod | BI72 | Peak Power Limiting | C: For Function
BO21 | Enable Active Power Following Mode #2 (Load Following) | Disable | Enable | DWFL2.Mod | BI73 | Load Following | C: For Function
BO22 | Enable Active Power Following Mode #3 (Generation Following) | Disable | Enable | DWFL3.Mod | BI74 | Generation Following | C: For Function
BO23 | Enable Automatic Generation Control Mode | Disable | Enable | DAGC.Mod | BI75 | AGC | C: For Function
BO24 | Enable Active Power Smoothing Mode | Disable | Enable | DWSM.Mod | BI76 | Active Power Smoothing | C: For Function
BO25 | Enable Volt-Watt Mode | Disable | Enable | DVWC.Mod | BI77 | Volt-Watt | C: For Function | M
BO26 | Enable Frequency-Watt Curve Mode | Disable | Enable | DHFW2.Mod | BI78 | Freq-Watt Curve | C: For Function
BO27 | Enable Constant Vars Mode | Disable | Enable | DVAR.Mod | BI79 | Const Vars | C: For Function | M
BO28 | Enable Constant Power Factor Mode | Disable | Enable | DFPF.Mod | BI80 | Constant PF | C: For Function | M
BO29 | Enable Volt-Var Control Mode | Disable | Enable | DVVR.Mod | BI81 | Volt-Var | C: For Function | M
BO30 | Enable Watt-Var Mode | Disable | Enable | DWVR.Mod | BI82 | Watt-Var | C: For Function
BO31 | Enable Power Factor Correction Mode | Disable | Enable | DPFC.Mod | BI83 | PF Correct | C: For Function
BO32 | Enable Pricing Mode | Disable | Enable | DPRG.Mod | BI84 | Price | C: For Function
BO33 | Enable Event-Based Reactive Current Support Mode. The moving average voltage and the base reactive current are frozen until after the voltage has returned to within the deadband for a specified hold time. Dynamic Reactive Current Support mode must be Enable for this setting to apply. | Disable | Enable | DRGS.ArGraMod | BI85 | Mode State | C: For Function
BO36 | Frequency-Watt Curve Mode - Use Hysteresis | Disable | Enable | DHFW1.HysEna | BI88 | Freq-Watt Curve | C: For Function
BO37 | Frequency-Watt Curve Mode - Snapshot of Power | Not Active | Active | DHFW1.SnptEna | BI89 | Freq-Watt Curve | C: For Function
BO38 | Charge/Discharge Mode - Use Ramp Rates. Indicates whether or not Charge/Discharge should use specified ramp rates or time constants. | Use Time Constants | Use Ramp Rates | DWGC.UseRmpRte | BI90 | Set Active Power | C: For Function
BO39 | AGC Mode - Use Ramp Rates. Indicates whether or not AGC mode should use specified ramp rates or time constants. | Use Time Constants | Use Ramp Rates | DAGC.UseRmpRte | BI91 | AGC | C: For Function
BO40 | Volt-Watt - Use Ramp Rates and Time Constants. Indicates whether Volt-Watt mode should use only Time Constants, or both Time Constants and Ramp Rates | Use Time Constants | Use Ramp Rates AND Time Constants | DVWC.UseRmpRte | BI92 | Volt-Watt | C: For Function
BO41 | Volt-Var Enable Autonomous Voltage Reference Adjustment | Disable | Enable | DVVR.VRefAdjEna | BI93 | Volt-Var | C: For Function | M
BO43 | Enable Renewable Energy Charging | Disable | Enable | DREN.Mod | BI110 | Renewable energy charging | C: For Function
BO44 | Enable Frequency-Watt Droop Function. Use Watts per Hz | Percent | Watts | DHFW3.Mod | BI112 | Droop Freq-Watt | C: For Function if Type is modifiable | M as watts
BO45 | Set Type of Active Power Limit. Use Percent or Watts | Percent | Watts | DWMX1.Mod | BI113 | Active Power Limit | C: For Function if Type is modifiable
BO46 | Set Type of Charge/Discharge target to % WMax or to Watts | Percent | Watts | DWGC1.Mod | BI114 | Charge/Discharge | C: For Function if Type is modifiable
BO47 | Set Constant Vars to use percent or vars | Percent | Vars | DVAR.1Mod | BI115 | Constant Vars | C: For Function if Type is modifiable | M as vars
BO2000 | Selected Schedule is Ready | Disable | Enable | BC.FSCHn.SchdSt.3 | BI2000 | BC Scheduling | C: If Back Comp Scheduling is used
BO2001 | Set Selected Schedule Repeat Weekly Sunday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.1 | BI2001 | BC Scheduling | C: If Back Comp Scheduling is used
BO2002 | Set Selected Schedule Repeat Weekly Monday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.2 | BI2002 | BC Scheduling | C: If Back Comp Scheduling is used
BO2003 | Set Selected Schedule Repeat Weekly Tuesday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.3 | BI2003 | BC Scheduling | C: If Back Comp Scheduling is used
BO2004 | Set Selected Schedule Repeat Weekly Wednesday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.4 | BI2004 | BC Scheduling | C: If Back Comp Scheduling is used
BO2005 | Set Selected Schedule Repeat Weekly Thursday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.5 | BI2005 | BC Scheduling | C: If Back Comp Scheduling is used
BO2006 | Set Selected Schedule Repeat Weekly Friday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.6 | BI2006 | BC Scheduling | C: If Back Comp Scheduling is used
BO2007 | Set Selected Schedule Repeat Weekly Saturday | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.7 | BI2007 | BC Scheduling | C: If Back Comp Scheduling is used
BO3000 | Submit Selected Schedule for Validation | Not Submitted | Submitted | FSCHn.SchdSt.2 | BI3000 | Scheduling | C: If 1815.2 Sched is used
BO3001 | Enable Selected Schedule | Disable | Enable | FSCHn.SchdSt.3 | BI3001 | Scheduling | C: If 1815.2 Sched is used
BO3002 | Set Selected Schedule Repeat Weekly Sunday | Do Not Repeat | Repeat | FSCHn.SchdReuse.1 | BI3002 | Scheduling | C: If 1815.2 Sched is used
BO3003 | Set Selected Schedule Repeat Weekly Monday | Do Not Repeat | Repeat | FSCHn.SchdReuse.2 | BI3003 | Scheduling | C: If 1815.2 Sched is used
BO3004 | Set Selected Schedule Repeat Weekly Tuesday | Do Not Repeat | Repeat | FSCHn.SchdReuse.3 | BI3004 | Scheduling | C: If 1815.2 Sched is used
BO3005 | Set Selected Schedule Repeat Weekly Wednesday | Do Not Repeat | Repeat | FSCHn.SchdReuse.4 | BI3005 | Scheduling | C: If 1815.2 Sched is used
BO3006 | Set Selected Schedule Repeat Weekly Thursday | Do Not Repeat | Repeat | FSCHn.SchdReuse.5 | BI3006 | Scheduling | C: If 1815.2 Sched is used
BO3007 | Set Selected Schedule Repeat Weekly Friday | Do Not Repeat | Repeat | FSCHn.SchdReuse.6 | BI3007 | Scheduling | C: If 1815.2 Sched is used
BO3008 | Set Selected Schedule Repeat Weekly Saturday | Do Not Repeat | Repeat | FSCHn.SchdReuse.7 | BI3008 | Scheduling | C: If 1815.2 Sched is used
BO30000 | Enable Volt-Watt Advanced Mode | Disable | Enable | DVWC1.Mod | BI30001 | Volt-Watt Advanced | C: For Function
BO30010 | Enable Synthetic Inertia Function | Disable | Enable | DSYN.Mod | BI30010 | Synthetic Inertia | C: For Function

## BI
DNP3 Point Index | Name / Description | Default Event Class | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Assoc. BO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BI0 | System Communication Error | 1 | Normal | Alarm: Communications error exists in the ESS | LCCH1.ChLiv |  | Alarm | M | M
BI1 | System Has Priority 1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH.GrAlm |  | Alarm | M | M
BI21 | DER is Off but Available to Start | 2 | Null | Off-Available | DGEN.DEROpSt.disconnectedandavailable |  | Monitoring | M | M
BI22 | DER is Off and Not Available to Start | 2 | Null | Off-Not-Available | DGEN.DEROpSt.disconnectedandblocked |  | Monitoring | M | M
BI25 | Islanded Mode. Determines how the DER behaves when in an Islanded configuration. <0> Isochronous Mode. DER attempts to control voltage and frequency independent of configured curves and settings up to the limits of the machine's capabilities in order to achieve the AO Reference Voltage and AO nominal frequency. <1> Droop Mode. DER acts as a follower using Volt/VAR and Freq/Watt curves. | 3 | Isochronous Mode | Droop Mode | DGEN.IsldCtlFol | BO6 | State | C: If in microgrid configuration
BI26 | Sensed Grid Config Detection Enabled. If Enabled, the DER may independently change its Active Settings Group based on locally observed grid conditions. <0> No Autonomous Detection. <1> Autonomous Detection. Inverter's Active Settings Group may differ from the Requested Settings Group | 3 | Not Ready | Ready | DECP.ECPIsldAuto | BO7 | State | C: If in microgrid configuration
BI27 | Storage Capacity Units. Determines whether energy storage values are expressed in units of Amp-hrs or Watt-hrs. | 3 | Amp-hrs (default) | Watt-hrs | DSTO.AGra | BO8 | State | C: For Storage
BI29 | Power Factor Excitation When Discharging / Generating | 2 | Injecting VARs - Q1 | Absorbing VARs - Q4 | DFPF.PFGnExtSet | BO10 | State | M
BI30 | Power Factor Excitation When Charging | 2 | Injecting VARs - Q2 | Absorbing VARs - Q3 | DFPF.PFLodExtSet | BO11 | State | M
BI31 | Supports Low/High Voltage Ride-Through Mode | 0 | Not Supported | Supported | DHVT |  | Volt Ride-Through | M | M
BI32 | Supports Low/High Frequency Ride-Through Mode | 0 | Not Supported | Supported | DHFT |  | Freq Ride-Through | M | M
BI33 | Supports Dynamic Reactive Current Support Mode | 0 | Not Supported | Supported | DRGS |  | Dyn React Curr Supp | M
BI34 | Supports Dynamic Volt-Watt Mode | 0 | Not Supported | Supported | DVWD |  | Dyn Volt-Watt | M
BI35 | Supports Frequency-Watt Mode | 0 | Not Supported | Supported | DHFW |  | Freq-Watt | M | M
BI36 | Supports Active Power Limit Mode | 0 | Not Supported | Supported | DWMX |  | Active Power Limit | M | M
BI37 | Supports Charge/Discharge Mode | 0 | Not Supported | Supported | DWGC |  | Set Active Power | M
BI38 | Supports Coordinated Charge/Discharge Mode | 0 | Not Supported | Supported | DTCD |  | Coord Charge-Dischg | M
BI39 | Supports Active Power Response Mode #1 (Peak Power Limiting) | 0 | Not Supported | Supported | DWFL1 |  | Peak Power Limiting | M
BI40 | Supports Active Power Response Mode #2 (Load Following) | 0 | Not Supported | Supported | DWFL2 |  | Load Following | M
BI41 | Supports Active Power Response Mode #3 (Generation Following) | 0 | Not Supported | Supported | DWFL3 |  | Generation Following | M
BI42 | Supports Automatic Generation Control Mode | 0 | Not Supported | Supported | DAGC |  | AGC | M
BI43 | Supports Active Power Smoothing Mode | 0 | Not Supported | Supported | DWSM |  | Active Power Smoothing | M
BI44 | Supports Volt-Watt Mode | 0 | Not Supported | Supported | DVWC |  | Volt-Watt | M | M
BI45 | Supports Frequency-Watt Curve Mode | 0 | Not Supported | Supported | DFWC |  | Freq-Watt Curve | M
BI46 | Supports Constant VArs Mode | 0 | Not Supported | Supported | DVAR |  | Const Vars | M | M
BI47 | Supports Constant Power Factor Mode | 0 | Not Supported | Supported | DFPF |  | Constant PF | M | M
BI48 | Supports Volt-VAr Control Mode | 0 | Not Supported | Supported | DVVR |  | Volt-Var | M | M
BI49 | Supports Watt-VAr Mode | 0 | Not Supported | Supported | DWVR |  | Watt-Var | M | M
BI50 | Supports Power Factor Correction Mode | 0 | Not Supported | Supported | DPFC |  | PF Correct | M
BI51 | Supports Pricing Mode | 0 | Not Supported | Supported | DPRG |  | Price | M
BI52 | Overvoltage Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTOV.Blk |  | Prot State | M
BI53 | Overvoltage Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTOV.Str.general |  | Prot State | M
BI54 | Overvoltage Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTOV.Op.general |  | Prot State | M
BI55 | Undervoltage Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTUV.Blk |  | Prot State | M
BI56 | Undervoltage Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTUV.Str.general |  | Prot State | M
BI57 | Undervoltage Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTUV.Op.general |  | Prot State | M
BI58 | Over Frequency Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTOF.Blk |  | Prot State | M
BI59 | Over Frequency Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTOF.Str.general |  | Prot State | M
BI60 | Over Frequency Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTOF.Op.general |  | Prot State | M
BI61 | Under Frequency Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTUF.Blk |  | Prot State | M
BI62 | Under Frequency Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTUF.Str.general |  | Prot State | M
BI63 | Under Frequency Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTUF.Op.general |  | Prot State | M
BI64 | Operating Mode - Low/High Voltage Ride-Through | 2 | Disabled | Enabled | DHVT.Mod | BO12 | Volt Ride-Through | C: For Function
BI65 | Operating Mode - Low/High Frequency Ride-Through | 2 | Disabled | Enabled | DHFT.Mod | BO13 | Freq Ride-Through | C: For Function
BI66 | Operating Mode - Dynamic Reactive Current Support Enabled | 2 | Disabled | Enabled | DRGS.Mod | BO14 | Dyn React Curr Supp | C: For Function
BI67 | Operating Mode - Dynamic Volt-Watt Enabled | 2 | Disabled | Enabled | DVWD.Mod | BO15 | Dyn Volt-Watt | C: For Function
BI68 | Operating Mode - Frequency-Watt Enabled | 2 | Disabled | Enabled | DHFW1.Mod | BO16 | Freq-Watt | C: For Function
BI69 | Operating Mode - Active Power Limit Enabled | 2 | Disabled | Enabled | DWMX.Mod | BO17 | Active Power Limit | C: For Function | M
BI70 | Operating Mode - Charge/Discharge Enabled | 2 | Disabled | Enabled | DWGC.Mod | BO18 | Set Active Power | C: For Function
BI71 | Operating Mode - Coordinated Charge / Discharge Management Enabled | 2 | Disabled | Enabled | DTCD.Mod | BO19 | Coord Charge-Dischg | C: For Function
BI72 | Operating Mode - Active Power Following Mode #1 (Peak Power Limiting) Enabled | 2 | Disabled | Enabled | DWFL1.Mod | BO20 | Peak Power Limiting | C: For Function
BI73 | Operating Mode - Active Power Following Mode #2 (Load Following) Enabled | 2 | Disabled | Enabled | DWFL2.Mod | BO21 | Load Following | C: For Function
BI74 | Operating Mode - Active Power Following Mode #3 (Generation Following) Enabled | 2 | Disabled | Enabled | DWFL3.Mod | BO22 | Generation Following | C: For Function
BI75 | Operating Mode - Automatic Generation Control Enabled | 2 | Disabled | Enabled | DAGC.Mod | BO23 | AGC | C: For Function
BI76 | Operating Mode - Active Power Smoothing Enabled | 2 | Disabled | Enabled | DWSM.Mod | BO24 | Active Power Smoothing | C: For Function
BI77 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWC.Mod | BO25 | Volt-Watt | C: For Function | M
BI78 | Operating Mode - Frequency-Watt Curve Enabled | 2 | Disabled | Enabled | DHFW2.Mod | BO26 | Freq-Watt Curve | C: For Function
BI79 | Operating Mode - Constant VArs Enabled | 2 | Disabled | Enabled | DVAR.Mod | BO27 | Const Vars | C: For Function | M
BI80 | Operating Mode - Constant Power Factor Enabled | 2 | Disabled | Enabled | DFPF.Mod | BO28 | Constant PF | C: For Function | M
BI81 | Operating Mode - Volt-VAR Control Enabled | 2 | Disabled | Enabled | DVVR.Mod | BO29 | Volt-Var | C: For Function | M
BI82 | Operating Mode - Watt-VAr Enabled | 2 | Disabled | Enabled | DWVR.Mod | BO30 | Watt-Var | C: For Function | M
BI83 | Operating Mode - Power Factor Correction Enabled | 2 | Disabled | Enabled | DPFC.Mod | BO31 | PF Correct | C: For Function
BI84 | Operating Mode - Pricing Enabled | 2 | Disabled | Enabled | DPRG.Mod | BO32 | Price | C: For Function
BI85 | Operating Mode - Event-Based Reactive Current Support Enabled | 2 | Disabled | Enabled | DRGS.ArGraMod | BO33 | Mode State | C: For Function
BI90 | Charge/Discharge Mode - Use Ramp Rates. Indicates whether or not Charge/Discharge should use specified ramp rates or ramp times. | 2 | Use Time Constants | Use Ramp Rates | DWGC.UseRmpRte | BO38 | Set Active Power | C: For Function
BI91 | AGC Mode - Use Ramp Rates. Indicates whether or not charge/discharge should use specified ramp rates or ramp times. | 2 | Use Time Constants | Use Ramp Rates | DAGC.UseRmpRte | BO39 | AGC | C: For Function
BI92 | Volt-Watt - Use Ramp Rates and Time Constants | 2 | Use Time Constants | Use Ramp Rates AND Time Constants | DVWC.UseRmpRte | BO40 | Volt-Watt | C: For Function
BI93 | Volt-VAr Enable Autonomous Voltage Reference Adjustment | 2 | Disabled | Enabled | DVVR.VRefAdjEna | BO41 | Volt-Var | C: For Function
BI94 | System Meter Active Power is Too High | 1 | Normal | Alarm | SYS.MMXU.TotW.range.max |  | Alarm | M
BI95 | System Meter Active Power is Too Low | 1 | Normal | Alarm | SYS.MMXU.TotW.range.min |  | Alarm | M
BI96 | System Meter Reactive Power is Too High | 1 | Normal | Alarm | SYS.MMXU.TotVAr.range.max |  | Alarm | M
BI97 | System Meter Reactive Power is Too Low | 1 | Normal | Alarm | SYS.MMXU.TotVAr.range.min |  | Alarm | M
BI98 | System Meter Power Factor is Too High | 1 | Normal | Alarm | SYS.MMXU.TotPF.range.max |  | Alarm | M
BI99 | System Meter Power Factor is Too Low | 1 | Normal | Alarm | SYS.MMXU.TotPF.range.min |  | Alarm | M
BI100 | System Meter Phase A Voltage is Too High | 1 | Normal | Alarm | SYS.MMXU.PhV.phsA.range.max |  | Alarm | M
BI101 | System Meter Phase A Voltage is Too Low | 1 | Normal | Alarm | SYS.MMXU.PhV.phsA.range.min |  | Alarm | M
BI102 | System Meter Phase B Voltage is Too High | 1 | Normal | Alarm | SYS.MMXU.PhV.phsB.range.max |  | Alarm | M
BI103 | System Meter Phase B Voltage is Too Low | 1 | Normal | Alarm | SYS.MMXU.PhV.phsB.range.min |  | Alarm | M
BI104 | System Meter Phase C Voltage is Too High | 1 | Normal | Alarm | SYS.MMXU.PhV.phsC.range.max |  | Alarm | M
BI105 | System Meter Phase C Voltage is Too Low | 1 | Normal | Alarm | SYS.MMXU.PhV.phsC.range.min |  | Alarm | M
BI106 | System Meter Communication Error | 1 | Normal: No Active Communications Error | Alarm: Active Communications Error | LCCH2.ChLiv |  | Alarm | M
BI107 | Selected Curve is Referenced by a Mode | 1 | Curve is not Referenced | Curve is Referenced | MESA.CrvRef |  | Curve | M
BI110 | Renewables only charging status | 2 | Disabled | Enabled | DREN.Mod | BO43 | Renewable energy charging | C: For Function
BI112 | Operating Mode - Frequency-Watt Droop Function. Using Watts per Hz | 2 | Percent | Watts | DHFW3.Mod | BO44 | Droop Freq-Watt | C: For Function | M as watts
BI113 | Type of Active Power Limit. Use Percent or Watts | 2 | Percent | Watts | DWMX1.Mod | BO45 | Active Power Limit | C: For Function
BI114 | Type of Charge/Discharge Target. Use percent or watts | 2 | Percent | Watts | DWGCX1.Mod | BO46 | Charge/Discharge | C: For Function
BI115 | Constant Vars. Use percent or vars | 2 | Percent | Vars | DVAR1.Mod | BO47 | Constant Vars | C: For Function | M as vars
BI2000 | Selected Schedule is Ready | 2 | Not Validated | Validated | BC.FSCHn.SchdSt.2 | BO2000 | BC Scheduling | C: For BC Scheduling
BI2001 | Selected Schedule Repeat Weekly Sunday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.1 | BO2001 | BC Scheduling | C: For BC Scheduling
BI2002 | Selected Schedule Repeat Weekly Monday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.2 | BO2002 | BC Scheduling | C: For BC Scheduling
BI2003 | Selected Schedule Repeat Weekly Tuesday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.3 | BO2003 | BC Scheduling | C: For BC Scheduling
BI2004 | Selected Schedule Repeat Weekly Wednesday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.4 | BO2004 | BC Scheduling | C: For BC Scheduling
BI2005 | Selected Schedule Repeat Weekly Thursday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.5 | BO2005 | BC Scheduling | C: For BC Scheduling
BI2006 | Selected Schedule Repeat Weekly Friday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.6 | BO2006 | BC Scheduling | C: For BC Scheduling
BI2007 | Selected Schedule Repeat Weekly Saturday | 2 | Do Not Repeat | Repeat | BC.FSCHn.SchdReuse.7 | BO2007 | BC Scheduling | C: For BC Scheduling
BI3000 | Selected Schedule is Validated by Outstation | 2 | Not Validated | Validated | FSCHn.SchdSt.2 | BO3000 | Scheduling | C: For 1815.2 Scheduling
BI3001 | Selected Schedule Is Enabled by Controlling Station | 2 | Disabled | Enabled | FSCHn.SchdSt.3 | BO3001 | Scheduling | C: For 1815.2 Scheduling
BI3002 | Selected Schedule Repeat Weekly Sunday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.1 | BO3002 | Scheduling | C: For 1815.2 Scheduling
BI3003 | Selected Schedule Repeat Weekly Monday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.2 | BO3003 | Scheduling | C: For 1815.2 Scheduling
BI3004 | Selected Schedule Repeat Weekly Tuesday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.3 | BO3004 | Scheduling | C: For 1815.2 Scheduling
BI3005 | Selected Schedule Repeat Weekly Wednesday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.4 | BO3005 | Scheduling | C: For 1815.2 Scheduling
BI3006 | Selected Schedule Repeat Weekly Thursday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.5 | BO3006 | Scheduling | C: For 1815.2 Scheduling
BI3007 | Selected Schedule Repeat Weekly Friday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.6 | BO3007 | Scheduling | C: For 1815.2 Scheduling
BI3008 | Selected Schedule Repeat Weekly Saturday | 2 | Do Not Repeat | Repeat | FSCHn.SchdReuse.7 | BO3008 | Scheduling | C: For 1815.2 Scheduling
BI5000 | Active Power at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotW.range |  | Equipment Data
BI5001 | Active Power at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotW.range |  | Equipment Data
BI5002 | Reactive Power at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotVAr.range |  | Equipment Data
BI5003 | Reactive Power at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotVAr.range |  | Equipment Data
BI5004 | Power Factor at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.TotPF.range |  | Equipment Data
BI5005 | Power Factor at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.TotPF.range |  | Equipment Data
BI5006 | Phase A Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsA.range |  | Equipment Data
BI5007 | Phase A Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsA.range |  | Equipment Data
BI5008 | Phase B Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsB.range |  | Equipment Data
BI5009 | Phase B Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsB.range |  | Equipment Data
BI5010 | Phase C Voltage at Meter #1 is Too High | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsC.range |  | Equipment Data
BI5011 | Phase C Voltage at Meter #1 is Too Low | 1 | Normal | Alarm | Meter1.MMXU.PhV.phsC.range |  | Equipment Data
BI5012 | Meter #1 Communication Error | 1 | Normal: No Active Communications Error | Alarm: Active Communications Error | Meter1.LCCH.ChLiv |  | Equipment Data
BI10000 | DER Unit #1 Is In Maintenance Operational State | 1 | Not in Maintenance | In Maintenance | DER_Unit1.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI10001 | DER Unit #1 Has P1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | DER_Unit1.CALH.GrAlm |  | Equipment Data
BI10002 | DER Unit #1 Has P2 Alarms | 1 | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | DER_Unit1.CALH.GrWrn |  | Equipment Data
BI10003 | DER Unit #1 Has P3 Alarms | 1 | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | DER_Unit1.CALH.GrInd |  | Equipment Data
BI15000 | Inverter #1 Active Power Output is Too High | 1 | Normal | Alarm | Inverter1.MMXU.TotW.range |  | Equipment Data
BI15001 | Inverter #1 Active Power Output is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.TotW.range |  | Equipment Data
BI15002 | Inverter #1 Reactive Power Output is Too High | 1 | Normal | Alarm | Inverter1.MMXU.TotVAr.range |  | Equipment Data
BI15003 | Inverter #1 Reactive Power Output is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.TotVAr.range |  | Equipment Data
BI15004 | Inverter #1 Current Output Frequency is Too High | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15005 | Inverter #1 Current Output Frequency is Too Low | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15006 | Inverter #1 DC Input Power is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Watt.range |  | Equipment Data
BI15007 | Inverter #1 DC Input Power is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Watt.range |  | Equipment Data
BI15008 | Inverter #1 DC Current Level is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Amp.range |  | Equipment Data
BI15009 | Inverter #1 DC Current Level is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Amp.range |  | Equipment Data
BI15010 | Inverter #1 DC Input Voltage is Too High | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15011 | Inverter #1 DC Input Voltage is Too Low | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15012 | Inverter #1 DNP3 Power Factor Excitation. Operating quadrant of the inverter. | 1 | Overexcited (producing VARs - Q1/Q2) | Underexcited (absorbing VARs - Q3/Q4) | Inverter1.DSTO.PFExtSet |  | Equipment Data
BI15013 | Inverter #1 Communication Error | 1 | Normal | Alarm | Inverter1.LCCH.ChLiv |  | Equipment Data
BI15014 | Inverter #1 Is In Local Control Mode | 1 | Normal | Alarm | Inverter1.DSTO.DEROpSt.disconnectedandinmaintenance |  | Equipment Data
BI15015 | Inverter #1 Is DC Contactor Closed | 1 | Normal | Alarm | Inverter1.DINV.InvSwiAlm |  | Equipment Data
BI15016 | Inverter #1 Ground Fault Alarm | 1 | Normal | Alarm | Inverter1.PDIS.Str |  | Equipment Data
BI15017 | Inverter #1 DC Over Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15018 | Inverter #1 DC Under Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMDC.Vol.range |  | Equipment Data
BI15019 | Inverter #1 AC Disconnect Warning | 1 | Normal | Alarm | Inverter1.DINV.InvACLosAlm |  | Equipment Data
BI15020 | Inverter #1 DC Disconnect Warning | 1 | Normal | Alarm | Inverter1.DINV.InvDCLosAlm |  | Equipment Data
BI15021 | Inverter #1 Grid Disconnect Warning | 1 | Normal | Inverter does not detect power on the grid | Inverter1.DINV.InvGriLosAlm |  | Equipment Data
BI15022 | Inverter #1 Cabinet Open Warning | 1 | Normal | Alarm | Inverter1.SPSE.GteSt.open |  | Equipment Data
BI15023 | Inverter #1 Manual Shutdown Warning | 1 | Normal | Alarm | Inverter1.DINV.InvManStopSt |  | Equipment Data
BI15024 | Inverter #1 Over Temperature Alarm | 1 | Normal | Alarm | Inverter1.DINV.EnclTmp.range |  | Equipment Data
BI15025 | Inverter #1 Under Temperature Alarm | 1 | Normal | Alarm | Inverter1.DINV.EnclTmp.range |  | Equipment Data
BI15026 | Inverter #1 Over Frequency Alarm | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15027 | Inverter #1 Under Frequency Alarm | 1 | Normal | Alarm | Inverter1.MMXU.Hz.range |  | Equipment Data
BI15028 | Inverter #1 AC Over Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMXU.PhV.PhsA.range |  | Equipment Data
BI15029 | Inverter #1 AC Under Voltage Alarm | 1 | Normal | Alarm | Inverter1.MMXU.PhV.PhsA.range |  | Equipment Data
BI15030 | Inverter #1 Blown String Fuse Alarm | 1 | Normal | Alarm | Inverter1.XFUS.FuSt |  | Equipment Data
BI15031 | Inverter #1 Memory Loss Alarm | 1 | Normal | Alarm | Inverter1.MESA.MemLosAlm |  | Equipment Data
BI15032 | Inverter #1 Hardware Test Failure | 1 | Normal | Alarm | Inverter1.DINV.TestRsl |  | Equipment Data
BI15033 | Inverter #1 Other Alarm | 1 | Normal | Alarm | Inverter1.CALH.GrAlm |  | Equipment Data
BI15034 | Inverter #1 Other Warning | 1 | Normal | Alarm | Inverter1.CALH.GrWrn |  | Equipment Data
BI20000 | Battery Bank #1 Status of Storage | 3 | Dis-connected | Connected | Battery1.DBAT.BatSt.connected |  | Equipment Data
BI20001 | Battery Bank #1 Communication Error | 1 | Normal | Alarm | Battery1.LCCH.ChLiv |  | Equipment Data
BI20002 | Battery Bank #1 Is In Local Control Mode | 1 | Not in Local Control | In Local Control | Battery1.DBAT.BatSt.localcontrol |  | Equipment Data
BI20003 | Battery Bank #1 Is DC Contactor Closed | 1 | Not Closed | Closed | Battery1.DBAT.DCSwCls |  | Equipment Data
BI20004 | Battery Bank #1 Is Charging | 1 | Not Charging | Charging | Battery1.DBAT.ChaSt |  | Equipment Data
BI20005 | Battery Bank #1 Is Discharging | 1 | Not Discharging | Discharging | Battery1.DBAT.DschSt |  | Equipment Data
BI20006 | Battery Bank #1 External Voltage is Too High | 1 | Normal | Alarm | Battery1.DBAT.ExtVolHiAlm |  | Equipment Data
BI20007 | Battery Bank #1 External Voltage is Too Low | 1 | Normal | Alarm | Battery1.DBAT.ExtVolLoAlm |  | Equipment Data
BI20008 | Battery Bank #1 Internal Voltage is Too High | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiAlm |  | Equipment Data
BI20009 | Battery Bank #1 Internal Voltage is Too Low | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoAlm |  | Equipment Data
BI20010 | Battery Bank #1 Over Temperature Alarm | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpHiAlm |  | Equipment Data
BI20011 | Battery Bank #1 Under Temperature Alarm | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpLoAlm |  | Equipment Data
BI20012 | Battery Bank #1 Temperature Imbalance Alarm | 1 | Normal | Alarm | Battery1.DBAT.UnbTmpAlm |  | Equipment Data
BI20013 | Battery Bank #1 Over Temperature Warning | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpHiWrn |  | Equipment Data
BI20014 | Battery Bank #1 Under Temperature Warning | 1 | Normal | Alarm | Battery1.DBAT.ExtTmpLoWrn |  | Equipment Data
BI20015 | Battery Bank #1 Temperature Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbTmpWrn |  | Equipment Data
BI20016 | Battery Bank #1 Over Charge Current Alarm | 1 | Normal | Alarm | Battery1.DBAT.ChaAmpHiAlm |  | Equipment Data
BI20017 | Battery Bank #1 Over Discharge Current Alarm | 1 | Normal | Alarm | Battery1.DBAT.DschAmpHiAlm |  | Equipment Data
BI20018 | Battery Bank #1 Over Charge Current Warning | 1 | Normal | Alarm | Battery1.DBAT.ChaAmpHiWrn |  | Equipment Data
BI20019 | Battery Bank #1 Over Discharge Current Warning | 1 | Normal | Alarm | Battery1.DBAT.DschAmpHiWrn |  | Equipment Data
BI20020 | Battery Bank #1 Voltage Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbVolWrn |  | Equipment Data
BI20021 | Battery Bank #1 Current Imbalance Warning | 1 | Normal | Alarm | Battery1.DBAT.UnbAmpWrn |  | Equipment Data
BI20022 | Battery Bank #1 Over Voltage Alarm | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiAlm |  | Equipment Data
BI20023 | Battery Bank #1 Under Voltage Alarm | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoAlm |  | Equipment Data
BI20024 | Battery Bank #1 Over Voltage Warning | 1 | Normal | Alarm | Battery1.DBAT.IntnVolHiWrn |  | Equipment Data
BI20025 | Battery Bank #1 Under Voltage Warning | 1 | Normal | Alarm | Battery1.DBAT.IntnVolLoWrn |  | Equipment Data
BI20026 | Battery Bank #1 Over State of Charge Maximum Alarm | 1 | Normal | Alarm | Battery1.DBAT.SocHiAlm |  | Equipment Data
BI20027 | Battery Bank #1 Under State of Charge Minimum Alarm | 1 | Normal | Alarm | Battery1.DBAT.SocLoAlm |  | Equipment Data
BI20028 | Battery Bank #1 Over State of Charge Maximum Warning | 1 | Normal | Alarm | Battery1.DBAT.SocHiWrn |  | Equipment Data
BI20029 | Battery Bank #1 Under State of Charge Minimum Warning | 1 | Normal | Alarm | Battery1.DBAT.SocLoWrn |  | Equipment Data
BI20030 | Battery Bank #1 Contactor Failure | 1 | Normal | Alarm | Battery1.MESA.ContFail |  | Equipment Data
BI20031 | Battery Bank #1 Fan Error | 1 | Normal | Alarm | Battery1.MESA.FanErr |  | Equipment Data
BI20032 | Battery Bank #1 Ground Fault | 1 | Normal | Alarm | Battery1.MESA.GndFlt |  | Equipment Data
BI20033 | Battery Bank #1 Door Open Alarm | 1 | Normal | Alarm | Battery1.MESA.DoorOpnAlm |  | Equipment Data
BI20034 | Battery Bank #1 Configuration Error | 1 | Normal | Alarm | Battery1.MESA.ConfErr |  | Equipment Data
BI20035 | Battery Bank #1 Configuration Warning | 1 | Normal | Alarm | Battery1.MESA.ConfWrn |  | Equipment Data
BI20036 | Battery Bank #1 Other Alarm | 1 | Normal | Alarm | Battery1.MESA.OthAlm |  | Equipment Data
BI20037 | Battery Bank #1 Other Warning | 1 | Normal | Alarm | Battery1.MESA.OthWrn |  | Equipment Data
BI20038 | Battery Bank #1 Fire Alarm | 1 | Normal | Alarm | Battery1.SFIR.FireAlm |  | Equipment Data
BI20039 | Battery Bank #1 Fire Supervisory Warning | 1 | Normal | Alarm | Battery1.MESA.FireSupWrn |  | Equipment Data
BI20040 | Battery Bank #1 Fire Trouble Warning | 1 | Normal | Alarm | Battery1.MESA.FireWrn |  | Equipment Data
BI20041 | Battery Bank #1 Fire Power Fault Warning | 1 | Normal | Alarm | Battery1.MESA.FireFltWrn |  | Equipment Data
BI20042 | Battery Bank #1 Chiller Alarm | 1 | Normal | Alarm | Battery1.MESA.ClAlm |  | Equipment Data
BI20043 | Battery Bank #1 Chiller Warning | 1 | Normal | Alarm | Battery1.MESA.ClWrn |  | Equipment Data
BI20044 | Battery Bank #1 Air Handler Alarm | 1 | Normal | Alarm | Battery1.MESA.AirCtlAlm |  | Equipment Data
BI20045 | Battery Bank #1 Air Handler Warning | 1 | Normal | Alarm | Battery1.MESA.AirCtlWrn |  | Equipment Data
BI20046 | Battery Bank #1 Fluid Alarm | 1 | Normal | Alarm | Battery1.MESA.FluAlm |  | Equipment Data
BI20047 | Battery Bank #1 Fluid Warning | 1 | Normal | Alarm | Battery1.MESA.FluWrn |  | Equipment Data
BI20048 | Battery Bank #1 Gas Alarm | 1 | Normal | Alarm | Battery1.MESA.GasAlm |  | Equipment Data
BI20049 | Battery Bank #1 Gas Warning | 1 | Normal | Alarm | Battery1.MESA.GasWrn |  | Equipment Data
BI20050 | Battery Bank #1 Electrolyte Alarm | 1 | Normal | Alarm | Battery1.MESA.ElcytAlm |  | Equipment Data
BI20051 | Battery Bank #1 Electrolyte Warning | 1 | Normal | Alarm | Battery1.MESA.ElcytWrn |  | Equipment Data
BI20052 | Battery Bank #1 Electrical Alarm | 1 | Normal | Alarm | Battery1.MESA.ElcAlm |  | Equipment Data
BI20053 | Battery Bank #1 Electrical Warning | 1 | Normal | Alarm | Battery1.MESA.ElcWrn |  | Equipment Data
BI30001 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWC1.Mod | BO30000 | Volt-Watt Advanced | C: For Function
BI30010 | Supports Synthetic Inertia Function | 0 | Not Supported | Supported | DSYN |  | Synthetic Inertia | C: For Function
BI30011 | Operating Mode - Synthetic Inertia Enabled | 2 | Disabled | Enabled | DSYN.Mod | BO30010 | Synthetic Inertia | C: For Function

## AO
DNP3 Point Index | Name / Description | Transmitted Value |  | Scaling |  | Units | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  | Minimum | Maximum | Multiplier | OffSet |  | IEC61850UniqueString | Assoc. AI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AO22 | Low/High Voltage Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.EcpRef | AI71 | Volt Ride-Through | C: For Function, unless set at implementation
AO23 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV1.BlkRef | AI73 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO24 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV1.BlkRef | AI74 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO25 | Low/High Voltage Ride-Through High Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV2.BlkRef | AI75 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO26 | Low/High Voltage Ride-Through Low Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV2.BlkRef | AI76 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO27 | Low/High Frequency Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.EcpRef | AI77 | Freq Ride-Through | C: For Function, unless set at implementation
AO28 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF1.BlkRef | AI79 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO29 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF1.BlkRef | AI80 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO30 | Low/High Frequency Ride-Through High Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation/discharging must stop when the frequency is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF2.BlkRef | AI81 | Freq Ride-Through | C: For Function, unless set at implementation
AO31 | Low/High Frequency Ride-Through Low Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation/discharging must stop when the frequency is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF2.BlkRef | AI82 | Freq Ride-Through | C: For Function, unless set at implementation
AO36 | Dynamic Reactive Current Support Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DRGS.EcpRef | AI87 | Dyn React Curr Supp | C: For Function, unless set at implementation
AO37 | Dynamic Reactive Current Support - Gradient Mode. Enumeration: <0> Undefined <1> Gradients reach 0 at the moving average Voltage <2> Gradients reach 0 at the Voltage deadbands | 0 | 2 | 1 | 0 | Enum | DRGS.ArGraMod | AI91 | Dyn React Curr Supp | C: For Function
AO38 | Dynamic Reactive Current Support Deadband Minimum Voltage. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays above this value for the length of the Hold Time. | -10000 | 0 | 0.1 | 0 | Percent | DRGS.DbVMin | AI92 | Dyn React Curr Supp | C: For Function
AO39 | Dynamic Reactive Current Support Deadband Maximum Voltage. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays below this value for the length of the Hold Time. | 0 | 10000 | 0.1 | 0 | Percent | DRGS.DbVMax | AI93 | Dyn React Curr Supp | C: For Function
AO40 | Dynamic Reactive Current Support Gradient for Sags. Percentage of the rated current (DRAT.ARtg) to apply capacitively per percentage of the negative deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSag | AI94 | Dyn React Curr Supp | C: For Function
AO41 | Dynamic Reactive Current Support Gradient for Swells. Percentage of the rated current (DRAT.ARtg) to apply inductively per percentage of the positive deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSwl | AI95 | Dyn React Curr Supp | C: For Function
AO42 | Dynamic Reactive Current Support Filter Time for Moving Average Voltage (RDGS.VAv). Used to determine amount of dynamic reactive current support. | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.FilTms | AI96 | Dyn React Curr Supp | C: For Function
AO43 | Dynamic Reactive Current Support Block Zone Voltage. Percentage of the nominal voltage (DRCT.VRef) below which no reactive current support shall be applied. | 0 | 1000 | 0.1 | 0 | Percent | DRGS.BlkZnV | AI97 | Dyn React Curr Supp | C: For Function
AO44 | Dynamic Reactive Current Support Hysteresis Block Zone Voltage. Percentage of the nominal voltage (DRCT.VRef). After being blocked, reactive current support shall not resume until the voltage has been above BlkZnV + HysBlkZnV. | 0 | 1000 | 0.1 | 0 | Percent | DRGS.HysBlkZnV | AI98 | Dyn React Curr Supp | C: For Function
AO45 | Dynamic Reactive Current Support Block Zone Time. Time in milliseconds from the beginning of any "sag" event, before which dynamic reactive current support will always continue, regardless of how low voltage may sag. | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.BlkZnTmms | AI99 | Dyn React Curr Supp | C: For Function
AO46 | Dynamic Reactive Current Support Start Hold Time. When the voltage exceeds the deadband limits for this length of time (measured in milliseconds), the "sag" or "swell" event begins and the DER may begin altering active power output. | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.HoldTmms | AI100 | Dyn React Curr Supp | C: For Function
AO47 | Dynamic Reactive Current Support End Hold Time. When the voltage returns to within the deadband limits for this length of time (measured in milliseconds), the "sag" or "swell" event is considered to be over. Reactive current support ends, frozen values are unfrozen, and a new event can begin. | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.HoldTmms.1 | AI101 | Dyn React Curr Supp | C: For Function
AO52 | Dynamic Volt-Watt Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVWD2.EcpRef | AI106 | Dyn Volt-Watt | C: For Function, unless set at implementation
AO53 | Dynamic Volt-Watt Gradient. Signed unit-less quantity that establishes the ratio of additional Watts supplied (expressed in terms of % DRCT.WMax) to the present difference from the moving average voltage (expressed as % DRCT.VRef). | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent voltage difference | DVWD.DynVWGra | AI110 | Dyn Volt-Watt | C: For Function
AO54 | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.VWFilTms | AI111 | Dyn Volt-Watt | C: For Function
AO55 | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage (DRCT.Vref) measured below the moving average voltage. If the present voltage is above this value, no additional Watts shall be supplied. | 0 | 1000 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWLo | AI112 | Dyn Volt-Watt | C: For Function
AO56 | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage (DRCT.Vref) measured above the moving average voltage. If the present voltage is below this value, no additional Watts shall be supplied. | 0 | 1000 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWHi | AI113 | Dyn Volt-Watt | C: For Function
AO61 | Frequency-Watt Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DHFW1.EcpRef | AI119 | Freq-Watt | C: For Function, unless set at implementation
AO62 | Frequency-Watt High Starting Frequency | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | AI121 | Freq-Watt | C: For Function | M
AO64 | Frequency-Watt High Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | AI123 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO476 | M
AO66 | Frequency-Watt Low Starting Frequency | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | AI125 | Freq-Watt | C: For Function | M
AO68 | Frequency-Watt Low Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | AI127 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO477 | M
AO72 | Frequency-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.1 | AI131 | Freq-Watt |  | M
AO73 | Frequency-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | AI132 | Freq-Watt |  | M
AO86 | Active Power Limit Signal Meter ID. (POC, PCC, or Other) | 0 | 2147483647 | 1 | 0 | n/a | DWMX.EcpRef | AI146 | Active Power Limit | C: For Function, unless set at implementation
AO87 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | AI148 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO478 | M
AO88 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | AI149 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO479 | M
AO93 | Charge/Discharge Active Power Target | -1000 | 1000 | 0.1 | 0 | Percent of WMax | DWGC.GnWPctSpt | AI154 | Set Active Power | C: For Function
AO94 | Charge/Discharge Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.1 | AI155 | Set Active Power | C: For Function
AO95 | Charge/Discharge Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.2 | AI156 | Set Active Power | C: For Function
AO96 | Charge/Discharge Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.DschRpuRte | AI157 | Set Active Power | C: For Function
AO97 | Charge/Discharge Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.DschRpdRte | AI158 | Set Active Power | C: For Function
AO98 | Charge/Discharge Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.ChaRpuRte | AI159 | Set Active Power | C: For Function
AO99 | Charge/Discharge Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.ChaRpdRte | AI160 | Set Active Power | C: For Function
AO100 | Charge/Discharge Minimum Reserve for Storage | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMinPct | AI161 | Set Active Power | C: For Function
AO101 | Charge/Discharge Maximum Reserve for Storage | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMaxPct | AI162 | Set Active Power | C: For Function
AO106 | Coordinated Charge/Discharge Target State of Charge | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DTCD.SocUseTgtPct | AI167 | Coord Charge-Dischg | C: For Function
AO107 | Coordinated Charge/Discharge Target Date | 0 | 2147483647 | 1 | 0 | Days | DTCD.DateTgt.Date | AI168 | Coord Charge-Dischg | C: For Function
AO108 | Coordinated Charge/Discharge Target Time | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.DateTgt.Time | AI169 | Coord Charge-Dischg | C: For Function
AO109 | Coordinated Charge/Discharge Energy Request | 0 | 2147483647 | 1 | 0 | Watt-hours | DTCD.WhReq | AI170 | Coord Charge-Dischg | C: For Function
AO110 | Coordinated Charge/Discharge Minimum Charging Duration | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurTms | AI171 | Coord Charge-Dischg | C: For Function
AO111 | Coordinated Charge/Discharge Date of Reference | 0 | 2147483647 | 1 | 0 | Days | DTCD.SocDate | AI172 | Coord Charge-Dischg | C: For Function
AO112 | Coordinated Charge/Discharge Time of Reference | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.SocDateTms | AI173 | Coord Charge-Dischg | C: For Function
AO113 | Coordinated Charge/Discharge Duration at Maximum Charge Rate | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurMax | AI174 | Coord Charge-Dischg | C: For Function
AO114 | Coordinated Charge/Discharge Duration at Maximum Discharge Rate | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.DschDurMax | AI175 | Coord Charge-Dischg | C: For Function
AO119 | Active Power Following Mode #1 (Peak Power Limiting) Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWFL1.EcpRef | AI180 | Peak Power Limiting | C: For Function, unless set at implementation
AO120 | Active Power Following Mode #1 (Peak Power Limiting) Power Threshold | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.FolWThr | AI182 | Peak Power Limiting | C: For Function
AO121 | Active Power Following Mode #1 (Peak Power Limiting) Ratio. Percent of the power exceeding the Power Threshold | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL1.FolWPct | AI183 | Peak Power Limiting | C: For Function
AO122 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpuRte | AI184 | Peak Power Limiting | C: For Function
AO123 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpdRte | AI185 | Peak Power Limiting | C: For Function
AO128 | Active Power Following Mode #2 (Load Following) Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWFL2.EcpRef | AI191 | Load Following | C: For Function, unless set at implementation
AO129 | Active Power Following Mode #2 (Load Following) Power Threshold | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.FolWThr | AI193 | Load Following | C: For Function
AO130 | Active Power Following Mode #2 (Load Following) Ratio. Percent of the power exceeding the Power Threshold | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL2.FolWPct | AI194 | Load Following | C: For Function
AO131 | Active Power Following Mode #2 (Load Following) Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpuRte | AI195 | Load Following | C: For Function
AO132 | Active Power Following Mode #2 (Load Following) Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpdRte | AI196 | Load Following | C: For Function
AO137 | Active Power Following Mode #3 (Generation Following) Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWFL3.EcpRef | AI202 | Generation Following | C: For Function, unless set at implementation
AO138 | Active Power Following Mode #3 (Generation Following) Power Threshold | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.FolWThr | AI204 | Generation Following | C: For Function
AO139 | Active Power Following Mode #3 (Generation Following) Ratio. Percent of the power exceeding the Power Threshold | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL3.FolWPct | AI205 | Generation Following | C: For Function
AO140 | Active Power Following Mode #3 (Generation Following) Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpuRte | AI206 | Generation Following | C: For Function
AO141 | Active Power Following Mode #3 (Generation Following) Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpdRte | AI207 | Generation Following | C: For Function
AO146 | AGC Active Power Target | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WSpt | AI213 | AGC | C: For Function
AO147 | AGC Ramp Time Constant Up Time | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.OplTmsMax.1 | AI214 | AGC | C: For Function
AO148 | AGC Ramp Time Constant Down Time | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.OplTmsMax.2 | AI215 | AGC | C: For Function
AO149 | AGC Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.DschRpuRte | AI216 | AGC | C: For Function
AO150 | AGC Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.DschRpdRte | AI217 | AGC | C: For Function
AO151 | AGC Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.ChaRpuRte | AI218 | AGC | C: For Function
AO152 | AGC Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.ChaRpdRte | AI219 | AGC | C: For Function
AO153 | AGC Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMinPct | AI220 | AGC | C: For Function
AO154 | AGC Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMaxPct | AI221 | AGC | C: For Function
AO159 | Active Power Smoothing Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWSM.EcpRef | AI231 | Active Power Smoothing | C: For Function, unless set at implementation
AO161 | Active Power Smoothing Lower Limit | -2147483648 | 0 | 1 | 0 | Watts | DWSM.WSmthLoLim | AI234 | Active Power Smoothing | C: For Function
AO162 | Active Power Smoothing Upper Limit | 0 | 2147483647 | 1 | 0 | Watts | DWSM.WSmthHiLim | AI235 | Active Power Smoothing | C: For Function
AO163 | Active Power Smoothing Filter Time (Seconds) | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.FilTms | AI236 | Active Power Smoothing | C: For Function
AO164 | Active Power Smoothing Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.DschRpuRte | AI237 | Active Power Smoothing | C: For Function
AO165 | Active Power Smoothing Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.DschRpdRte | AI238 | Active Power Smoothing | C: For Function
AO166 | Active Power Smoothing Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.ChaRpuRte | AI239 | Active Power Smoothing | C: For Function
AO167 | Active Power Smoothing Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.ChaRpdRte | AI240 | Active Power Smoothing | C: For Function
AO172 | Volt-Watt Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVWC.EcpRef | AI246 | Volt-Watt | C: For Function, unless set at implementation
AO173 | Volt-Watt Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVWC.VWCrv | AI248 | Volt-Watt | C: For Function, unless set at implementation as zero | C: See clause 1.7
AO174 | Volt-Watt Filter Time (Seconds) | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.FilTms | AI250 | Volt-Watt | C: For Function
AO175 | Volt-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.1 | AI251 | Volt-Watt | C: For Function | M
AO176 | Volt-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.2 | AI252 | Volt-Watt | C: For Function | M
AO177 | Volt-Watt Discharging Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.DschRpuRte | AI253 | Volt-Watt | C: For Function
AO178 | Volt-Watt Discharging Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.DschRpdRte | AI254 | Volt-Watt | C: For Function
AO179 | Volt-Watt Charging Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.ChaRpuRte | AI255 | Volt-Watt | C: For Function
AO180 | Volt-Watt Charging Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC.ChaRpdRte | AI256 | Volt-Watt | C: For Function
AO185 | Frequency-Watt Curve Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.EcpRef | AI261 | Freq-Watt Curve | C: For Function, unless set at implementation
AO186 | Frequency-Watt Curve - Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HzWCrv | AI263 | Freq-Watt Curve | C: For Function
AO187 | Frequency-Watt Curve - High Frequency Hysteresis Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HysCrv | AI264 | Freq-Watt Curve | C: For Function
AO188 | Frequency-Watt Curve - Low Frequency Hysteresis Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DLFW2.HysCrv | AI265 | Freq-Watt Curve | C: For Function
AO189 | Frequency-Watt Curve Start Delay | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStrDlTmms | AI266 | Freq-Watt Curve | C: For Function
AO190 | Frequency-Watt Curve Stop Delay | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStopDlTmms | AI267 | Freq-Watt Curve | C: For Function
AO191 | Frequency-Watt Curve Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.1 |  | Freq-Watt Curve | C: For Function
AO192 | Frequency-Watt Curve Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.2 | AI269 | Freq-Watt Curve | C: For Function
AO193 | Frequency-Watt Curve Discharge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuRte | AI270 | Freq-Watt Curve | C: For Function
AO194 | Frequency-Watt Curve Discharge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdRte | AI271 | Freq-Watt Curve | C: For Function
AO195 | Frequency-Watt Curve Charge Ramp Up Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuChaRte | AI272 | Freq-Watt Curve | C: For Function
AO196 | Frequency-Watt Curve Charge Ramp Down Rate | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdChaRte | AI273 | Freq-Watt Curve | C: For Function
AO197 | Frequency-Watt Curve Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMinPct | AI275 | Freq-Watt Curve | C: For Function
AO198 | Frequency-Watt Curve Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMaxPct | AI276 | Freq-Watt Curve | C: For Function
AO203 | Constant Vars Reactive Power Target | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | AI281 | Const Vars | C: For Function | M
AO204 | Constant Vars Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.1 | AI282 | Const Vars | C: For Function
AO205 | Constant Vars Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.2 | AI283 | Const Vars | C: For Function
AO210 | Constant Power Factor Setpoint - Generation/Discharging | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | AI288 | Constant PF | C: For Function | M
AO211 | Constant Power Factor Setpoint - Charging | 0 | 100 | 0.01 | 0 | None | DFPF.PFLodTgt | AI289 | Constant PF | C: For Function | M
AO216 | Volt-Var Control Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVVR.EcpRef | AI294 | Volt-Var | C: For Function, unless set at implementation
AO217 | Volt-Var Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVVR.VVArCrv | AI297 | Volt-Var | C: For Function | M
AO218 | Volt-Var Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.1 | AI298 | Volt-Var | C: For Function
AO219 | Volt-Var Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.2 | AI299 | Volt-Var | C: For Function
AO220 | Volt-Var Autonomous Voltage Reference Adjustment Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.VRefTmms | AI300 | Volt-Var | C: For Function | M
AO225 | Watt-Var Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DWVR.EcpRef | AI306 | Watt-Var | C: For Function, unless set at implementation
AO226 | Watt-Var Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DWVR.WVArCrv | AI308 | Watt-Var | C: For Function
AO227 | Watt-Var Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.1 | AI309 | Watt-Var | C: For Function
AO228 | Watt-Var Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.2 | AI310 | Watt-Var | C: For Function
AO233 | Power Factor Correction Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DPFC.EcpRef | AI316 | PF Correct | C: For Function, unless set at implementation
AO234 | Power Factor Correction Average PF Target | -100 | 100 | 0.01 | 0 | None | DPFC.PFTrg | AI318 | PF Correct | C: For Function
AO235 | Power Factor Correction Lower PF Limit | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.min | AI319 | PF Correct | C: For Function
AO236 | Power Factor Correction Upper PF Limit | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.max | AI320 | PF Correct | C: For Function
AO244 | Curve Edit Selector. Writing to this point selects which of the curves can currently be viewed and changed. | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | AI328 | Curve | C: See clause 1.7 | C: See clause 1.7
AO245 | Curve Type. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-Var <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | AI329 | Curve | C: See clause 1.7 | C: See clause 1.7
AO246 | Curve Number of Points | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | AI330 | Curve | C: See clause 1.7 | C: See clause 1.7
AO247 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time (milliseconds) <23> Celsius Temperature <29> Voltage (V) <33> Frequency (Hz) <38> Watts (W) <100> Price in hundredths of local currency <129> Percent Voltage <133> Percent Frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | AI331 | Curve | C: See clause 1.7 | C: See clause 1.7
AO248 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> Vars as percent of max Vars (VarMax) <3> Vars as percent of max available Vars (VarAval) <4> Vars as percent of max Watts (Wmax) - not used <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor <8> Volts as a percent of the nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage (V) <33> Frequency (Hz) <38> Watts (W) <99+> Other | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | AI332 | Curve | C: See clause 1.7 | C: See clause 1.7
AO249 | Curve Point 1 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | AI333 | Curve | C: See clause 1.7 | C: See clause 1.7
AO250 | Curve Point 1 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | AI334 | Curve | C: See clause 1.7 | C: See clause 1.7
AO251 | Curve Point 2 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | AI335 | Curve | C: See clause 1.7 | C: See clause 1.7
AO252 | Curve Point 2 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | AI336 | Curve | C: See clause 1.7 | C: See clause 1.7
AO253 | Curve Point 3 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | AI337 | Curve | C: See clause 1.7 | C: See clause 1.7
AO254 | Curve Point 3 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | AI338 | Curve | C: See clause 1.7 | C: See clause 1.7
AO255 | Curve Point 4 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | AI339 | Curve | C: See clause 1.7 | C: See clause 1.7
AO256 | Curve Point 4 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | AI340 | Curve | C: See clause 1.7 | C: See clause 1.7
AO257 | Curve Point 5 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.xVal | AI341 | Curve | C: See clause 1.7
AO258 | Curve Point 5 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.yVal | AI342 | Curve | C: See clause 1.7
AO259 | Curve Point 6 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.xVal | AI343 | Curve | C: See clause 1.7
AO260 | Curve Point 6 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.yVal | AI344 | Curve | C: See clause 1.7
AO261 | Curve Point 7 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.xVal | AI345 | Curve | C: See clause 1.7
AO262 | Curve Point 7 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.yVal | AI346 | Curve | C: See clause 1.7
AO263 | Curve Point 8 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.xVal | AI347 | Curve | C: See clause 1.7
AO264 | Curve Point 8 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.yVal | AI348 | Curve | C: See clause 1.7
AO265 | Curve Point 9 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.xVal | AI349 | Curve | C: See clause 1.7
AO266 | Curve Point 9 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.yVal | AI350 | Curve | C: See clause 1.7
AO267 | Curve Point 10 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.xVal | AI351 | Curve | C: See clause 1.7
AO268 | Curve Point 10 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.yVal | AI352 | Curve | C: See clause 1.7
AO269 | Curve Point 11 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.11.xVal | AI353 | Curve | C: See clause 1.7
AO270 | Curve Point 11 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.11.yVal | AI354 | Curve | C: See clause 1.7
AO271 | Curve Point 12 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.12.xVal | AI355 | Curve | C: See clause 1.7
AO272 | Curve Point 12 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.12.yVal | AI356 | Curve | C: See clause 1.7
AO273 | Curve Point 13 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.13.xVal | AI357 | Curve | C: See clause 1.7
AO274 | Curve Point 13 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.13.yVal | AI358 | Curve | C: See clause 1.7
AO275 | Curve Point 14 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.14.xVal | AI359 | Curve | C: See clause 1.7
AO276 | Curve Point 14 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.14.yVal | AI360 | Curve | C: See clause 1.7
AO277 | Curve Point 15 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.15.xVal | AI361 | Curve | C: See clause 1.7
AO278 | Curve Point 15 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.15.yVal | AI362 | Curve | C: See clause 1.7
AO279 | Curve Point 16 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.16.xVal | AI363 | Curve | C: See clause 1.7
AO280 | Curve Point 16 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.16.yVal | AI364 | Curve | C: See clause 1.7
AO281 | Curve Point 17 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.17.xVal | AI365 | Curve | C: See clause 1.7
AO282 | Curve Point 17 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.17.yVal | AI366 | Curve | C: See clause 1.7
AO283 | Curve Point 18 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.18.xVal | AI367 | Curve | C: See clause 1.7
AO284 | Curve Point 18 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.18.yVal | AI368 | Curve | C: See clause 1.7
AO285 | Curve Point 19 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.19.xVal | AI369 | Curve | C: See clause 1.7
AO286 | Curve Point 19 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.19.yVal | AI370 | Curve | C: See clause 1.7
AO287 | Curve Point 20 X-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.20.xVal | AI371 | Curve | C: See clause 1.7
AO288 | Curve Point 20 Y-Value | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.20.yVal | AI372 | Curve | C: See clause 1.7
AO473 | Renewable energy source. Max rated active power (WMaxRtg) which may result from renewable energy resource | 0 | 2147483647 | 1 | 0 | Watts | RenWMaxRtg | AI582 | Renewable energy source | C: For Function
AO474 | Max SOC for Active Power Following #1 (Peak Power Limiting) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMaxPct | AI584 | Peak Power Limiting | C: For Function
AO475 | Min SOC for Active Power Following #1 (Peak Power Limiting) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMinPct | AI585 | Peak Power Limiting | C: For Function
AO476 | Max SOC for Active Power Following #2 (Load Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMaxPct | AI586 | Load Following | C: For Function
AO477 | Min SOC for Active Power Following #2 (Load Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMinPct | AI587 | Load Following | C: For Function
AO478 | Max SOC for Active Power Following #3 (Generation Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMaxPct | AI588 | Generation Following | C: For Function
AO479 | Min SOC for Active Power Following #3 (Generation Following) | 0 | 2147483647 | 1 | 0 | SOC | DSTO.UseWhMinPct | AI589 | Generation Following | C: For Function
AO480 | High Frequency-Watt Droop Upper Gradient | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | AI590 | Droop Freq-Watt | C: For Function | M
AO481 | Low Frequency-Watt Droop Lower Gradient | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | AI591 | Droop Freq-Watt | C: For Function | M
AO482 | High Frequency-Watt Droop Minimum Active Power | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | AI592 | Droop Freq-Watt | C: For Function | M
AO483 | Low Frequency-Watt Droop Maximum Active Power | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | AI593 | Droop Freq-Watt | C: For Function | M
AO484 | Volt-Var 4 V-Q pairs Volt V1 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt1 | AI594 | Volt-Var | C: For Function
AO485 | Volt-Var 4 V-Q pairs Vars Q1 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt1 | AI595 | Volt-Var | C: For Function
AO486 | Volt-Var 4 V-Q pairs Volt V2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt2 | AI596 | Volt-Var | C: For Function
AO487 | Volt-Var 4 V-Q pairs Vars Q2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt2 | AI597 | Volt-Var | C: For Function
AO488 | Volt-Var 4 V-Q pairs Volt V3 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt3 | AI598 | Volt-Var | C: For Function
AO489 | Volt-Var 4 V-Q pairs Vars Q3 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt3 | AI599 | Volt-Var | C: For Function
AO490 | Volt-Var 4 V-Q pairs Volt V4 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVVR.VPctPt4 | AI600 | Volt-Var | C: For Function
AO491 | Volt-Var 4 V-Q pairs Vars Q4 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DVVR.VArPctPt4 | AI601 | Volt-Var | C: For Function
AO492 | Watt-Var 4 P-Q pairs Watt P1 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt1 | AI602 | Watt-Var | C: For Function
AO493 | Watt-Var 4 P-Q pairs Vars Q1 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt1 | AI603 | Watt-Var | C: For Function
AO494 | Watt-Var 4 P-Q pairs Watt P2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt2 | AI604 | Watt-Var | C: For Function
AO495 | Watt-Var 4 P-Q pairs Vars Q2 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt2 | AI605 | Watt-Var | C: For Function
AO496 | Watt-Var 4 P-Q pairs Watt P3 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt3 | AI606 | Watt-Var | C: For Function
AO497 | Watt-Var 4 P-Q pairs Vars Q3 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt3 | AI607 | Watt-Var | C: For Function
AO498 | Watt-Var 4 P-Q pairs Watt P4 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DWVR.WPctPt4 | AI608 | Watt-Var | C: For Function
AO499 | Watt-Var 4 P-Q pairs Vars Q4 | -2147483648 | 2147483647 | 1 | 0 | Vars as % of VAMax | DWVR.VArPctPt4 | AI609 | Watt-Var | C: For Function
AO500 | Volt-Watt 2 V-P pairs Volt V1 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC.VPctPt1 | AI610 | Volt-Watt | C: For Function
AO501 | Volt-Watt 2 V-P pairs Watt P1 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC.WPctPt1 | AI611 | Volt-Watt | C: For Function
AO502 | Volt-Watt 2 V-P pairs Volt V2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts as % of VRef | DVWC.VPctPt2 | AI612 | Volt-Watt | C: For Function
AO503 | Volt-Watt 2 V-P pairs Watt P2 | -2147483648 | 2147483647 | 1 | 0 | Watts as % of WMax | DVWC.WPctPt2 | AI613 | Volt-Watt | C: For Function
AO508 | Charge/Discharge target in Watts | -2147483648 | 2147483647 | 1 | 0 | Watts | DWGC.GnWSpt | AI618 | Charge/Discharge | C: For Function If BI114=1
AO509 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | AI619 | Active Power Limit | C: For Function if BI113 = 1 | M
AO510 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | AI620 | Active Power Limit | C: For Function if BI113 = 1 | M
AO511 | Constant Vars using vars as unit | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | AI621 | Constant Vars | C: For Function if BI115 = 1 | M
AO2000 | Schedule to Edit Selector. Selects which of the schedules can be currently viewed and changed. | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCC.Schd | AI2001 | BC Scheduling | C: For Back Comp
AO2001 | Selected Schedule Identity | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCCn.Schd | AI2002 | BC Scheduling | C: For Back Comp
AO2002 | Selected Schedule Priority. Priority of the schedule relative to other running schedules. Lower values have higher priority over higher values. | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCHn.SchdPrio | AI2003 | BC Scheduling | C: For Back Comp
AO2003 | Selected Schedule Type. Enumeration: <1> Low/High Voltage Ride-Through – Hi Must Trip <2> Low/High Voltage Ride-Through – Low Must Trip <3> Low/High Voltage Ride-Through – Hi Momentary <4> Low/High Voltage Ride-Through – Lo Momentary <5> Low/High Frequency Ride-Through – Hi Must Trip <6> Low/High Frequency Ride-Through – Lo Must Trip <7> Low/High Frequency Ride-Through – Hi Momentary <8> Low/High Frequency Ride-Through – Low Momentary <9> Dynamic Reactive Current Support - On/Off <10> Dynamic Volt-Watt - On/Off <11> Frequency-Watt - On/Off <12> Active Power Limit - Charging <13> Active Power Limit - Discharging <14> Charge/Discharge - Percent of Maximum <15> Coordinated Charge/Discharge - SOC Target <16> Active Power Response #1 - On/Off <17> Active Power Response #2 - On/Off <18> Active Power Response #3 - On/Off <19> AGC – Watts <20> Active Power Smoothing - On/Off <21> Volt-Watt – Curve Index <22> Frequency-Watt Curve – Curve Index <23> Frequency-Watt Curve – High Hysteresis <24> Frequency-Watt Curve – Low Hysteresis <25> Constant VArs - Percent of Maximum <26> Constant Power Factor - Power Factor <27> Volt-VAr – Curve Index <28> Watt-VAr – Curve Index <29> Power Factor Correction - On/Off <30> Reserved - For pricing mode <31> Charge/Discharge - enable/disable <32> Coordinated Charge/Discharge - enable/disable <33> Active Power Limit - Discharging - enable/disable <34> Active Power Response #1 - Limit <35> Active Power Response #2 - Limit <36> Active Power Response #3 - Limit <37> AGC - enable/disable ... <100> Vendor-specific enumerations above | 0 | 255 | 1 | 0 | Enum | MESAn.SchdVal.valEq | AI2004 | BC Scheduling | C: For Back Comp
AO2004 | Selected Schedule Start Date. Number of days since January 1, 1970, UTC. | 0 | 2147483647 | 1 | 0 | Days | BC.FSCHn.StrTm.Date | AI2005 | BC Scheduling | C: For Back Comp
AO2005 | Selected Schedule Start Time. Milliseconds since the start of Schedule Start Date. | 0 | 86400000 | 1 | 0 | milliseconds | BC.FSCHn.StrTm.Time | AI2006 | BC Scheduling | C: For Back Comp
AO2006 | Selected Schedule Repeat Interval. Interval between actions after the initial occurrence. A zero value means the schedule is not repeated. | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCHn.NxtStrTm | AI2007 | BC Scheduling | C: For Back Comp
AO2007 | Selected Schedule Repeat Interval Units. Enumeration: <0> = No Repeat <1> = Seconds <2> = Minutes <3> = Hours <4> = Days <5> = Weeks <6> = Months <7> = Months on Same Day of Week <8> = Months on Same Day of Week from End | 0 | 8 | 1 | 0 | Enum | BC.FSCHn.SchdReuse | AI2008 | BC Scheduling | C: For Back Comp
AO2008 | Selected Schedule Number of Points | 0 | 100 | 1 | 0 | n/a | BC.FSCHn.NumEntr | AI2011 | BC Scheduling | C: For Back Comp
AO2009 | Selected Schedule Point [1] Time Offset. Number of seconds from the start of the schedule when this point becomes active. | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.1 | AI2012 | BC Scheduling | C: For Back Comp
AO2010 | Selected Schedule Point [1] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.1 | AI2013 | BC Scheduling | C: For Back Comp
AO2011 | Selected Schedule Point [2] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.2 | AI2014 | BC Scheduling | C: For Back Comp
AO2012 | Selected Schedule Point [2] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.2 | AI2015 | BC Scheduling | C: For Back Comp
AO2013 | Selected Schedule Point [3] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.3 | AI2016 | BC Scheduling | C: For Back Comp
AO2014 | Selected Schedule Point [3] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.3 | AI2017 | BC Scheduling | C: For Back Comp
AO2015 | Selected Schedule Point [4] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.4 | AI2018 | BC Scheduling | C: For Back Comp
AO2016 | Selected Schedule Point [4] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.4 | AI2019 | BC Scheduling | C: For Back Comp
AO2017 | Selected Schedule Point [5] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.5 | AI2020 | BC Scheduling | C: For Back Comp
AO2018 | Selected Schedule Point [5] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.5 | AI2021 | BC Scheduling | C: For Back Comp
AO2019 | Selected Schedule Point [6] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.6 | AI2022 | BC Scheduling | C: For Back Comp
AO2020 | Selected Schedule Point [6] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.6 | AI2023 | BC Scheduling | C: For Back Comp
AO2021 | Selected Schedule Point [7] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.7 | AI2024 | BC Scheduling | C: For Back Comp
AO2022 | Selected Schedule Point [7] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.7 | AI2025 | BC Scheduling | C: For Back Comp
AO2023 | Selected Schedule Point [8] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.8 | AI2026 | BC Scheduling | C: For Back Comp
AO2024 | Selected Schedule Point [8] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.8 | AI2027 | BC Scheduling | C: For Back Comp
AO2025 | Selected Schedule Point [9] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.9 | AI2028 | BC Scheduling | C: For Back Comp
AO2026 | Selected Schedule Point [9] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.9 | AI2029 | BC Scheduling | C: For Back Comp
AO2027 | Selected Schedule Point [10] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.10 | AI2030 | BC Scheduling | C: For Back Comp
AO2028 | Selected Schedule Point [10] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.10 | AI2031 | BC Scheduling | C: For Back Comp
AO2029 | Selected Schedule Point [11] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.11 | AI2032 | BC Scheduling | C: For Back Comp
AO2030 | Selected Schedule Point [11] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.11 | AI2033 | BC Scheduling | C: For Back Comp
AO2031 | Selected Schedule Point [12] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.12 | AI2034 | BC Scheduling | C: For Back Comp
AO2032 | Selected Schedule Point [12] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.12 | AI2035 | BC Scheduling | C: For Back Comp
AO2033 | Selected Schedule Point [13] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.13 | AI2036 | BC Scheduling | C: For Back Comp
AO2034 | Selected Schedule Point [13] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.13 | AI2037 | BC Scheduling | C: For Back Comp
AO2035 | Selected Schedule Point [14] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.14 | AI2038 | BC Scheduling | C: For Back Comp
AO2036 | Selected Schedule Point [14] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.14 | AI2039 | BC Scheduling | C: For Back Comp
AO2037 | Selected Schedule Point [15] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.15 | AI2040 | BC Scheduling | C: For Back Comp
AO2038 | Selected Schedule Point [15] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.15 | AI2041 | BC Scheduling | C: For Back Comp
AO2039 | Selected Schedule Point [16] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.16 | AI2042 | BC Scheduling | C: For Back Comp
AO2040 | Selected Schedule Point [16] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.16 | AI2043 | BC Scheduling | C: For Back Comp
AO2041 | Selected Schedule Point [17] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.17 | AI2044 | BC Scheduling | C: For Back Comp
AO2042 | Selected Schedule Point [17] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.17 | AI2045 | BC Scheduling | C: For Back Comp
AO2043 | Selected Schedule Point [18] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.18 | AI2046 | BC Scheduling | C: For Back Comp
AO2044 | Selected Schedule Point [18] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.18 | AI2047 | BC Scheduling | C: For Back Comp
AO2045 | Selected Schedule Point [19] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.19 | AI2048 | BC Scheduling | C: For Back Comp
AO2046 | Selected Schedule Point [19] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.19 | AI2049 | BC Scheduling | C: For Back Comp
AO2047 | Selected Schedule Point [20] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.20 | AI2050 | BC Scheduling | C: For Back Comp
AO2048 | Selected Schedule Point [20] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.20 | AI2051 | BC Scheduling | C: For Back Comp
AO3000 | Schedule Index to Edit Selector. Selection of Schedule Index for viewing, creating, and updating that schedule | 0 | 2147483647 | 1 | 0 | n/a | FSCC.Schd | AI3000 | Scheduling | C: For Sched
AO3001 | Selected Schedule Identity. Assigned ID of the schedule which may be different from the Schedule Index | 0 | 2147483647 | 1 | 0 | n/a | FSCCn.Schd | AI3001 | Scheduling | C: For Sched
AO3002 | Selected Schedule Priority. Priority of the schedule relative to other running schedules. Lower values have higher priority over higher values. | 0 | 2147483647 | 1 | 0 | n/a | FSCHn.SchdPrio | AI3002 | Scheduling | C: For Sched
AO3003 | Selected Schedule Start Date. Number of days since January 1, 1970, UTC. | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | AI3003 | Scheduling | C: For Sched
AO3004 | Selected Schedule Start Time. Seconds since the start of Schedule Start Date. | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | AI3004 | Scheduling | C: For Sched
AO3005 | Selected Schedule Stop Date. Number of days since January 1, 1970, UTC. | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | AI3005 | Scheduling | C: For Sched
AO3006 | Selected Schedule Stop Time. Seconds since the stop of Schedule Stop Date. | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | AI3006 | Scheduling | C: For Sched
AO3007 | Selected Schedule Repeat Interval. Interval between actions after the initial occurrence. A zero value means the schedule is not repeated. | 0 | 2147483647 | 1 | 0 | n/a | FSCHn.NxtStrTm | AI3007 | Scheduling | C: For Sched
AO3008 | Selected Schedule Repeat Interval Units. Enumeration: <0> = No Repeat <1> = Seconds <2> = Minutes <3> = Hours <4> = Days <5> = Weeks <6> = Months <7> = Months on Same Day of Week <8> = Months on Same Day of Week from End | 0 | 8 | 1 | 0 | Enum | FSCHn.SchdReuse | AI3008 | Scheduling | C: For Sched
AO3009 | Selected Schedule Number of Points | 0 | 100 | 1 | 0 | n/a | FSCHn.NumEntr | AI3011 | Scheduling | C: For Sched
AO3010 | Selected Schedule Point [1] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.1 | AI3012 | Scheduling | C: For Sched
AO3011 | Selected Schedule Point [1] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.1 | AI3013 | Scheduling | C: For Sched
AO3012 | Selected Schedule Point [1] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.1 | AI3014 | Scheduling | C: For Sched
AO3013 | Selected Schedule Point [1] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.1 | AI3015 | Scheduling | C: For Sched
AO3014 | Selected Schedule Point [2] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.2 | AI3016 | Scheduling | C: For Sched
AO3015 | Selected Schedule Point [2] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.2 | AI3017 | Scheduling | C: For Sched
AO3016 | Selected Schedule Point [2] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.2 | AI3018 | Scheduling | C: For Sched
AO3017 | Selected Schedule Point [2] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.2 | AI3019 | Scheduling | C: For Sched
AO3018 | Selected Schedule Point [3] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.3 | AI3020 | Scheduling | C: For Sched
AO3019 | Selected Schedule Point [3] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.3 | AI3021 | Scheduling | C: For Sched
AO3020 | Selected Schedule Point [3] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.3 | AI3022 | Scheduling | C: For Sched
AO3021 | Selected Schedule Point [3] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.3 | AI3023 | Scheduling | C: For Sched
AO3022 | Selected Schedule Point [4] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.4 | AI3024 | Scheduling | C: For Sched
AO3023 | Selected Schedule Point [4] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.4 | AI3025 | Scheduling | C: For Sched
AO3024 | Selected Schedule Point [4] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.4 | AI3026 | Scheduling | C: For Sched
AO3025 | Selected Schedule Point [4] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.4 | AI3027 | Scheduling | C: For Sched
AO3026 | Selected Schedule Point [5] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.5 | AI3028 | Scheduling | C: For Sched
AO3027 | Selected Schedule Point [5] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.5 | AI3029 | Scheduling | C: For Sched
AO3028 | Selected Schedule Point [5] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.5 | AI3030 | Scheduling | C: For Sched
AO3029 | Selected Schedule Point [5] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.5 | AI3031 | Scheduling | C: For Sched
AO3030 | Selected Schedule Point [6] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.6 | AI3032 | Scheduling | C: For Sched
AO3031 | Selected Schedule Point [6] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.6 | AI3033 | Scheduling | C: For Sched
AO3032 | Selected Schedule Point [6] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.6 | AI3034 | Scheduling | C: For Sched
AO3033 | Selected Schedule Point [6] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.6 | AI3035 | Scheduling | C: For Sched
AO3034 | Selected Schedule Point [7] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.7 | AI3036 | Scheduling | C: For Sched
AO3035 | Selected Schedule Point [7] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.7 | AI3037 | Scheduling | C: For Sched
AO3036 | Selected Schedule Point [7] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.7 | AI3038 | Scheduling | C: For Sched
AO3037 | Selected Schedule Point [7] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.7 | AI3039 | Scheduling | C: For Sched
AO3038 | Selected Schedule Point [8] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.8 | AI3040 | Scheduling | C: For Sched
AO3039 | Selected Schedule Point [8] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.8 | AI3041 | Scheduling | C: For Sched
AO3040 | Selected Schedule Point [8] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.8 | AI3042 | Scheduling | C: For Sched
AO3041 | Selected Schedule Point [8] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.8 | AI3043 | Scheduling | C: For Sched
AO3042 | Selected Schedule Point [9] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.9 | AI3044 | Scheduling | C: For Sched
AO3043 | Selected Schedule Point [9] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.9 | AI3045 | Scheduling | C: For Sched
AO3044 | Selected Schedule Point [9] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.9 | AI3046 | Scheduling | C: For Sched
AO3045 | Selected Schedule Point [9] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.9 | AI3047 | Scheduling | C: For Sched
AO3046 | Selected Schedule Point [10] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.10 | AI3048 | Scheduling | C: For Sched
AO3047 | Selected Schedule Point [10] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.10 | AI3049 | Scheduling | C: For Sched
AO3048 | Selected Schedule Point [10] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.10 | AI3050 | Scheduling | C: For Sched
AO3049 | Selected Schedule Point [10] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.10 | AI3051 | Scheduling | C: For Sched
AO3050 | Selected Schedule Point [11] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.11 | AI3052 | Scheduling | C: For Sched
AO3051 | Selected Schedule Point [11] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.11 | AI3053 | Scheduling | C: For Sched
AO3052 | Selected Schedule Point [11] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.11 | AI3054 | Scheduling | C: For Sched
AO3053 | Selected Schedule Point [11] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.11 | AI3055 | Scheduling | C: For Sched
AO3054 | Selected Schedule Point [12] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.12 | AI3056 | Scheduling | C: For Sched
AO3055 | Selected Schedule Point [12] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.12 | AI3057 | Scheduling | C: For Sched
AO3056 | Selected Schedule Point [12] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.12 | AI3058 | Scheduling | C: For Sched
AO3057 | Selected Schedule Point [12] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.12 | AI3059 | Scheduling | C: For Sched
AO3058 | Selected Schedule Point [13] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.13 | AI3060 | Scheduling | C: For Sched
AO3059 | Selected Schedule Point [13] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.13 | AI3061 | Scheduling | C: For Sched
AO3060 | Selected Schedule Point [13] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.13 | AI3062 | Scheduling | C: For Sched
AO3061 | Selected Schedule Point [13] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.13 | AI3063 | Scheduling | C: For Sched
AO3062 | Selected Schedule Point [14] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.14 | AI3064 | Scheduling | C: For Sched
AO3063 | Selected Schedule Point [14] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.14 | AI3065 | Scheduling | C: For Sched
AO3064 | Selected Schedule Point [14] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.14 | AI3066 | Scheduling | C: For Sched
AO3065 | Selected Schedule Point [14] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.14 | AI3067 | Scheduling | C: For Sched
AO3066 | Selected Schedule Point [15] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.15 | AI3068 | Scheduling | C: For Sched
AO3067 | Selected Schedule Point [15] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.15 | AI3069 | Scheduling | C: For Sched
AO3068 | Selected Schedule Point [15] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.15 | AI3070 | Scheduling | C: For Sched
AO3069 | Selected Schedule Point [15] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.15 | AI3071 | Scheduling | C: For Sched
AO3070 | Selected Schedule Point [16] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.16 | AI3072 | Scheduling | C: For Sched
AO3071 | Selected Schedule Point [16] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.16 | AI3073 | Scheduling | C: For Sched
AO3072 | Selected Schedule Point [16] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.16 | AI3074 | Scheduling | C: For Sched
AO3073 | Selected Schedule Point [16] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.16 | AI3075 | Scheduling | C: For Sched
AO3074 | Selected Schedule Point [17] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.17 | AI3076 | Scheduling | C: For Sched
AO3075 | Selected Schedule Point [17] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.17 | AI3077 | Scheduling | C: For Sched
AO3076 | Selected Schedule Point [17] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.17 | AI3078 | Scheduling | C: For Sched
AO3077 | Selected Schedule Point [17] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.17 | AI3079 | Scheduling | C: For Sched
AO3078 | Selected Schedule Point [18] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.18 | AI3080 | Scheduling | C: For Sched
AO3079 | Selected Schedule Point [18] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.18 | AI3081 | Scheduling | C: For Sched
AO3080 | Selected Schedule Point [18] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.18 | AI3082 | Scheduling | C: For Sched
AO3081 | Selected Schedule Point [18] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.18 | AI3083 | Scheduling | C: For Sched
AO3082 | Selected Schedule Point [19] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.19 | AI3084 | Scheduling | C: For Sched
AO3083 | Selected Schedule Point [19] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.19 | AI3085 | Scheduling | C: For Sched
AO3084 | Selected Schedule Point [19] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.19 | AI3086 | Scheduling | C: For Sched
AO3085 | Selected Schedule Point [19] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.19 | AI3087 | Scheduling | C: For Sched
AO3086 | Selected Schedule Point [20] Time Offset | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.20 | AI3088 | Scheduling | C: For Sched
AO3087 | Selected Schedule Point [20] Action Type | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.20 | AI3089 | Scheduling | C: For Sched
AO3088 | Selected Schedule Point [20] Action Index | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.20 | AI3090 | Scheduling | C: For Sched
AO3089 | Selected Schedule Point [20] Value | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.20 | AI3091 | Scheduling | C: For Sched
AO5000 | Meter #1 Active Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.hLim | AI5025 | Equipment Data
AO5001 | Meter #1 Active Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.lLim | AI5026 | Equipment Data
AO5002 | Meter #1 Reactive Power – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.hLim | AI5027 | Equipment Data
AO5003 | Meter #1 at Reactive Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.lLim | AI5028 | Equipment Data
AO5004 | Meter #1 at Power Factor – High Threshold | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.hLim | AI5029 | Equipment Data
AO5005 | Meter #1 at Power Factor – Low Threshold | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.lLim | AI5030 | Equipment Data
AO5006 | Meter #1 Phase A Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.hLim | AI5031 | Equipment Data
AO5007 | Meter #1 Phase A Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.lLim | AI5032 | Equipment Data
AO5008 | Meter #1 Phase B Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.hLim | AI5033 | Equipment Data
AO5009 | Meter #1 Phase B Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.lLim | AI5034 | Equipment Data
AO5010 | Meter #1 Phase C Volts – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.hLim | AI5035 | Equipment Data
AO5011 | Meter #1 Phase C Volts – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.lLim | AI5036 | Equipment Data
AO15000 | Inverter #1 Active Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.hLim | AI15021 | Equipment Data
AO15001 | Inverter #1 Active Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.lLim | AI15022 | Equipment Data
AO15002 | Inverter #1 Reactive Power Output – High Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.hLim | AI15023 | Equipment Data
AO15003 | Inverter #1 Reactive Power Output – Low Threshold | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.lLim | AI15024 | Equipment Data
AO15004 | Inverter #1 Current Output Frequency – High Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.hLim | AI15025 | Equipment Data
AO15005 | Inverter #1 Current Output Frequency – Low Threshold | 0 | 70000 | 0.001 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.lLim | AI15026 | Equipment Data
AO15006 | Inverter #1 DC Inverter Input Power – High Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.hLim | AI15027 | Equipment Data
AO15007 | Inverter #1 DC Inverter Input Power – Low Threshold | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.lLim | AI15028 | Equipment Data
AO15008 | Inverter #1 DC Current Available – High Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter1.MMDC.Amp.RangeC.hLim | AI15029 | Equipment Data
AO15009 | Inverter #1 DC Current Available – Low Threshold | 0 | 2147483647 | 1 | 0.1 | Amps | Inverter1.MMDC.Amp.RangeC.lLim | AI15030 | Equipment Data
AO15010 | Inverter #1 DC Voltage Between DER System and Inverter – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.hLim | AI15031 | Equipment Data
AO15011 | Inverter #1 DC Voltage Between DER System and Inverter – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.lLim | AI15032 | Equipment Data
AO20000 | Battery Bank #1 External Voltage - High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolHiAls | AI20023 | Equipment Data
AO20001 | Battery Bank #1 External Voltage - Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolLoAls | AI20024 | Equipment Data
AO20002 | Battery Bank #1 Internal Voltage – High Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolHiAls | AI20025 | Equipment Data
AO20003 | Battery Bank #1 Internal Voltage – Low Threshold | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolLoAls | AI20026 | Equipment Data
AO30004 | Volt-Watt Adv Signal Meter ID | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | AI30004 | Volt-Watt Advanced | C: For Function
AO30005 | Volt-Watt Adv High Start Voltage Threshold. Voltage threshold for starting high voltage events. | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | AI30006 | Volt-Watt Advanced | C: For Function
AO30007 | Volt-Watt Adv Low Start Voltage Threshold. Voltage threshold for starting low voltage events. | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | AI30008 | Volt-Watt Advanced | C: For Function
AO30011 | Volt-Watt Adv Curve Index. Index of the Volt-Watt Adv curve that should be used by the m | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | AI30012 | Volt-Watt Advanced | C: For Function
AO30015 | Volt-Watt Adv Discharging Ramp Up Rate. Maximum ramp up rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuRte | AI30017 | Volt-Watt Advanced | C: For Function
AO30016 | Volt-Watt Adv Discharging Ramp Down Rate. Maximum ramp down rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdRte | AI30018 | Volt-Watt Advanced | C: For Function
AO30017 | Volt-Watt Adv Charging Ramp Up Rate. Maximum charging ramp up rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuChaRte | AI30019 | Volt-Watt Advanced | C: For Function
AO30018 | Volt-Watt Adv Charging Ramp Down Rate. Maximum charging ramp down rate. | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdChaRte | AI30020 | Volt-Watt Advanced | C: For Function
AO30019 | Volt-Watt Adv Minimum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMinPct | AI30021 | Volt-Watt Advanced | C: For Function
AO30020 | Volt-Watt Adv Maximum Usable SOC | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMaxPct | AI30022 | Volt-Watt Advanced | C: For Function

## AI
DNP3 Point Index | Name / Description | Default Event Class | Transmitted Value |  | Scaling |  | Units | IEC61850 | Additional Information |  |  |  |  | EUT Capabilities
|  |  | Minimum | Maximum | Multiplier | Offset |  | IEC61850UniqueString | Value | Assoc. AO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AI0 | DER Profile Version Number. | 3 | 100 | 10000 | 0.01 | 0 | n/a | MESA.VersNum | 1.1 |  | Nameplate | M
AI1 | DER Profile Implementation Level. 1, 2 or 3 to indicate support for Level 1, Level 2 or Level 3 respectively. 0 means ignore | 3 | 0 | 3 | 1 | 0 | n/a | MESA.ImplLvl | 0 |  | Nameplate | M
AI2 | Nameplate Minimum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMinRtg | 0 |  | Nameplate | M | M
AI3 | Nameplate Maximum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMaxRtg | 0 |  | Nameplate | M | M
AI4 | Nameplate Active Generation Power Rating at Unity Power Factor | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMaxRtg | 0 |  | Nameplate | M | M
AI5 | Nameplate Active Charging Power Rating at Unity Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWMaxRtg | 0 |  | Nameplate | C: For Storage
AI6 | Nameplate Active Generation Power Rating at Specified Over-Excited Power Factor, injecting reactive power (as positive vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WOvPFRtg | 0 |  | Nameplate | M | M
AI7 | Nameplate Active Charging Power Rating at Specified Over-Excited Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWOvPFRtg | 0 |  | Nameplate | C: For Storage
AI8 | Specified Over-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.OvPFRtg | 0 |  | Nameplate | M | M
AI9 | Nameplate Active Generation Power Rating at Specified Under-Excited Power Factor, absorbing reactive power (as negative vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WUnPFRtg | 0 |  | Nameplate | M | M
AI10 | Nameplate Active Charging Power Rating at Specified Under-Excited Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWUnPFRtg | 0 |  | Nameplate | M | M
AI11 | Specified Under-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.UnPFRtg | 0 |  | Nameplate | M | M
AI12 | Nameplate Reactive Supply (Injection) Power Rating | 3 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMaxRtg | 0 |  | Nameplate | M | M
AI13 | Nameplate Reactive Absorption Power Rating | 3 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMaxRtg | 0 |  | Nameplate | M | M
AI14 | Nameplate Apparent Generation Power Rating | 3 | 0 | 2147483647 | 1 | 0 | VAs | DGEN.VAMaxRtg | 0 |  | Nameplate | M
AI15 | Nameplate Apparent Charging Power Rating | 3 | -2147483648 | 0 | 1 | 0 | VAs | DSTO.ChaVAMaxRtg | 0 |  | Nameplate | M | M
AI16 | Nameplate Storage Actual Energy Capacity. Nameplate (original) actual total energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.WhRtg | 0 |  | Nameplate | C: For Storage | M
AI17 | Storage Effective Actual Energy Capacity. Present actual total energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.EffWh | 0 |  | Nameplate | C: For Storage
AI18 | Storage Usable Energy Capacity. Usable energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.UseWh | 0 |  | Nameplate | C: For Storage
AI19 | Nameplate AC Current Maximum Generation Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Amps | DGEN.AMaxRtg | 0 |  | Nameplate | M
AI20 | Nameplate AC Current Maximum Charging Rating | 3 | -2147483648 | 0 | 0.1 | 0 | Amps | DSTO.ChaAMaxRtg | 0 |  | Nameplate | C: For Storage
AI21 | Remaining Reactive Susceptance | 3 | -2147483648 | 2147483647 | 1 | 0 | Siemens | DGEN.SuscRtg | 0 |  | Nameplate |  | M
AI22 | IEEE 1547 Normal Operating Performance Category. Enumeration: <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DGEN.RegClas.1 | 0 |  | Nameplate | M | M
AI23 | IEEE 1547 Abnormal Operating Performance Category. Enumeration: <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DGEN.RegClas.2 | 0 |  | Nameplate | M | M
AI24 | Number of System Schedules | 3 | 0 | 100 | 1 | 0 | None | MESA.NumSchd | 0 |  | Config | M
AI25 | Number of Meters | 3 | 0 | 3 | 1 | 0 | None | MESA.NumMtr | 3 |  | Config | M
AI26 | Number of Inverters | 3 | 0 | 2 | 1 | 0 | None | MESA.NumInv | 2 |  | Config | M
AI27 | Number of Batteries | 3 | 0 | 2 | 1 | 0 | None | MESA.NumBat | 2 |  | Config | M
AI28 | Number of DER units connected to controller | 3 | 0 | 7 | 1 | 0 | None | DSTO.InclDER | 7 |  | Config | M
AI29 | Reference Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VRef | 0 | AO0 | Config | M | M
AI30 | Reference Voltage Offset | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts | DECP.VRefOfs | 0 | AO1 | Config | M | M
AI31 | Nominal Grid Frequency | 2 | 0 | 70000 | 0.001 | 0 | Hz | DECP.EcpHzNom | 0 | AO2 | Config | M
AI32 | Maximum Active Generation Power | 2 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMax | 0 |  | Operational Settings | M | M
AI33 | Maximum Active Charging Power | 2 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWMax | 0 |  | Operational Settings | C: For Storage
AI34 | Maximum Reactive Injection Power | 2 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMax | 0 |  | Operational Settings | M | M
AI35 | Maximum Reactive Absorption Power | 2 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMax | 0 |  | Operational Settings | M | M
AI36 | Maximum Apparent Generation Power | 2 | 0 | 2147483647 | 1 | 0 | VA | DGEN.VAMax | 0 |  | Operational Settings | M
AI37 | Maximum Apparent Charging Power | 2 | -2147483648 | 0 | 1 | 0 | VA | DSTO.ChaVAMax | 0 |  | Operational Settings | C: For Storage
AI38 | Minimum Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VMin | 0 |  | Operational Settings | M
AI39 | Maximum Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VMax | 0 |  | Operational Settings | M
AI40 | Open Loop Response Time Percentage. Percent of target to reach witInvertern the open loop response time. Default is 90%. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DGEN.OplPct | 0 |  | Operational Settings | M
AI41 | Power Factor Sign Convention. Enumeration: <1> IEC – active power <2> IEEE – lead/lag | 2 | 1 | 2 | 1 | 0 | None | PF.MMXU.PFSign | 1 | AO4 | Operational Settings | M
AI42 | Reference for Reactive Power Setpoints. Selects which setpoint is active. Default is <3>. <0> Not applicable / Unknown <1> Percent of Maximum Active Power (WMax) <2> Percent of Maximum Reactive Power (VArMax) <3> Percent of Available Reactive Power (VArAvl) | 2 | 0 | 3 | 1 | 0 | Enum | DGEN.VArSetRef | 0 | AO5 | Operational Settings | M | M set to <2>
AI43 | System Available Active Generation Power | 2 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.MMXU.TotW | 0 |  | Monitoring | M
AI44 | System Available Active Charging Power | 2 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.MMXU.TotChaW | 0 |  | Monitoring | C: For Storage
AI45 | System Available Reactive Injection Power | 2 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarAvl | 0 |  | Monitoring | M
AI46 | System Available Reactive Absorption Power | 2 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarAvl | 0 |  | Monitoring | M
AI47 | System Available Actual State of Charge. Present energy in the DER as a percentage of Storage Effective Actual Capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DSTO.SocPct | 0 |  | Monitoring | C: For Storage
AI48 | System Usable State of Charge. Present usable energy in the DER as a percentage of Nameplate Storage Usable Capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DSTO.UseSocPct | 0 |  | Monitoring | C: For Storage | M
AI49 | System Start-up Status | 2 | -1 | 99 | 1 | 0 | Enum | DGEN.DEROpSt | 0 |  | Monitoring | M
AI50 | DER Start (Return to Service) Voltage High Limit. Percent of Reference Voltage. | 2 | 0 | 20000 | 0.01 | 0 | Percent | DCTE1.VHiLim | 0 | AO6 | Return to Service | M
AI51 | DER Start (Return to Service) Voltage Low Limit. Percent of Reference Voltage. | 2 | 0 | 10000 | 0.01 | 0 | Percent | DCTE1.VLoLim | 0 | AO7 | Return to Service | M
AI52 | DER Start (Return to Service) Frequency High Limit | 2 | 0 | 70000 | 0.001 | 0 | Hz | DCTE1.HzHiLim | 0 | AO8 | Return to Service | M
AI53 | DER Start (Return to Service) Frequency Low Limit | 2 | 0 | 70000 | 0.001 | 0 | Hz | DCTE1.HzLoLim | 0 | AO9 | Return to Service | M
AI54 | DER Start (Return to Service) Delay | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE1.RtnDlTmms | 0 | AO10 | Return to Service | M
AI58 | DER Stop (Cease to Energize) Ramp Down Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DCTE2.RmpTms | 0 | AO14 | Cease | M
AI62 | Maximum Generation Ramp Up Rate. The maximum generation ramp up rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DCTE.RpuRteMax | 0 |  | Operational Settings | M
AI63 | Maximum Generation Ramp Down Rate. The maximum generation ramp down rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DCTE.RpdRteMax | 0 |  | Operational Settings | M
AI71 | Low/High Voltage Ride-Through Signal Meter ID. Referenced ECP. TInverters is the meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHVT.EcpRef | 0 | AO22 | Volt Ride-Through | C: For Function
AI72 | Low/High Voltage Ride-Through Voltage Reference Input. Active voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DHVT.MMXN.Vol | 0 |  | Volt Ride-Through | C: For Function
AI73 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV1.BlkRef | 0 | AO23 | Volt Ride-Through | C: For Function
AI74 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV1.BlkRef | 0 | AO24 | Volt Ride-Through | C: For Function
AI75 | Low/High Voltage Ride-Through High Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation / discharging must stop when the voltage is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV2.BlkRef | 0 | AO25 | Volt Ride-Through | C: For Function
AI76 | Low/High Voltage Ride-Through Low Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation / discharging must stop when the voltage is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV2.BlkRef | 0 | AO26 | Volt Ride-Through | C: For Function
AI77 | Low/High Frequency Ride-Through Signal Meter ID. Referenced ECP. TInverters is the meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFT.EcpRef | 0 | AO27 | Freq Ride-Through | C: For Function
AI78 | Low/High Frequency Ride-Through Frequency Reference Input. Active frequency measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DHFT.MMXU.Hz | 0 |  | Freq Ride-Through | C: For Function
AI79 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF1.BlkRef | 0 | AO28 | Freq Ride-Through | C: For Function
AI80 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF1.BlkRef | 0 | AO29 | Freq Ride-Through | C: For Function
AI81 | Low/High Frequency Ride-Through High Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation / discharging must stop when the frequency is High. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF2.BlkRef | 0 | AO30 | Freq Ride-Through | C: For Function
AI82 | Low/High Frequency Ride-Through Low Momentary Cessation Curve Index. Index of the Frequency Ride-through curve which specifies where generation / discharging must stop when the frequency is low. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF2.BlkRef | 0 | AO31 | Freq Ride-Through | C: For Function
AI83 | Dynamic Reactive Current Support Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DRGS.ModPrio | 0 | AO32 | Dyn React Curr Supp | C: For Function
AI87 | Dynamic Reactive Current Support Signal Meter ID. Referenced ECP meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DRGS.EcpRef | 0 | AO36 | Dyn React Curr Supp | C: For Function
AI88 | Dynamic Reactive Current Support Voltage Reference Input. Votltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DRGS.MMXN.Vol | 0 |  | Dyn React Curr Supp | C: For Function
AI89 | Dynamic Reactive Current Support Moving Average Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DRGS.VAv | 0 |  | Dyn React Curr Supp | C: For Function
AI90 | Dynamic Reactive Current Support Present Delta Voltage. Difference in Volts between the present measured Voltage and the Moving Average Voltage as a percentage of the reference voltage | 2 | -10000 | 10000 | 0.1 | 0 | Percent | DRGS.DelV | 0 |  | Dyn React Curr Supp | C: For Function
AI91 | Dynamic Reactive Current Support - Gradient Mode. Enumeration: <0> Undefined <1> Gradients reach 0 at the moving average Voltage <2> Gradients reach 0 at the Voltage deadbands | 2 | 0 | 2 | 1 | 0 | Enum | DRGS.ArGraMod | 0 | AO37 | Dyn React Curr Supp | C: For Function
AI92 | Dynamic Reactive Current Support Deadband Minimum Voltage. Percentage of the nominal voltage, measured from the moving average voltage. Support is no longer applied when the voltage stays above tInverters value for the length of the Hold Time. | 2 | -10000 | 0 | 0.1 | 0 | Percent | DRGS.DbVMin | 0 | AO38 | Dyn React Curr Supp | C: For Function
AI93 | Dynamic Reactive Current Support Deadband Maximum Voltage. Percentage of the nominal voltage, measured from the moving average voltage. Support is no longer applied when the voltage stays below tInverters value for the length of the Hold Time. | 2 | 0 | 10000 | 0.1 | 0 | Percent | DRGS.DbVMax | 0 | AO39 | Dyn React Curr Supp | C: For Function
AI94 | Dynamic Reactive Current Support Gradient for Sags. Percentage of the rated current to apply capacitively per percentage of the negative deviation from the moving average voltage. It is a ratio of percent and is therefore unitless. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSag | 0 | AO40 | Dyn React Curr Supp | C: For Function
AI95 | Dynamic Reactive Current Support Gradient for Swells. Percentage of the rated current to apply inductively per percentage of the positive deviation from the moving average voltage. It is a ratio of percent and is therefore unitless. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent current per percent voltage deviation | DRGS.ArGraSwl | 0 | AO41 | Dyn React Curr Supp | C: For Function
AI96 | Dynamic Reactive Current Support Filter Time for Moving Average Voltage. Used to determine amount of dynamic reactive current support. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DRGS.FilTms | 0 | AO42 | Dyn React Curr Supp | C: For Function
AI97 | Dynamic Reactive Current Support Block Zone Voltage. Percentage of the nominal voltage below which no reactive current support shall be applied. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DRGS.BlkZnV | 0 | AO43 | Dyn React Curr Supp | C: For Function
AI98 | Dynamic Reactive Current Support Hysteresis Block Zone Voltage. Percentage of the nominal voltage. After being blocked, reactive current support shall not resume until the voltage has been above the hysteresis block zone. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DRGS.HysBlkZnV | 0 | AO44 | Dyn React Curr Supp | C: For Function
AI99 | Dynamic Reactive Current Support Block Zone Time. Time in milliseconds from the beginning of any "sag" event, before which dynamic reactive current support will always continue, regardless of how low voltage may sag. | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.BlkZnTmms | 0 | AO45 | Dyn React Curr Supp | C: For Function
AI100 | Dynamic Reactive Current Support Hold Time. When the voltage returns to witInvertern the deadband limits for tInverters length of time (measured in milliseconds), the "sag" or "swell" event is considered to be over. Reactive current support ends, frozen values are unfrozen, and a new event can begin. | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DRGS.HoldTmms | 0 | AO47 | Dyn React Curr Supp | C: For Function
AI101 | Dynamic Reactive Current Attempted Output. Current output that the mode is attempting to achieve based on the Voltage input and other parameters. | 2 | 0 | 2147483647 | 0.1 | 0 | Amps | DRGS.ReqA | 0 |  | Dyn React Curr Supp | C: For Function
AI102 | Dynamic Volt-Watt Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVWD.ModPrio | 0 | AO48 | Dyn Volt-Watt | C: For Function
AI106 | Dynamic Volt-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWD.EcpRef | 0 | AO52 | Dyn Volt-Watt | C: For Function
AI107 | Dynamic Volt-Watt Voltage Reference Input. Votltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWD.MMXN.Vol | 0 |  | Dyn Volt-Watt | C: For Function
AI108 | Dynamic Volt-Watt Moving Average Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWD.VAv | 0 |  | Dyn Volt-Watt | C: For Function
AI109 | Dynamic Volt-Watt Present Delta Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWD.DelV | 0 |  | Dyn Volt-Watt | C: For Function
AI110 | Dynamic Volt-Watt Gradient. Signed quantity that establishes the ratio of additional Watts supplied to the present difference from the moving average voltage. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent voltage difference | DVWD.DynVWGra | 0 | AO53 | Dyn Volt-Watt | C: For Function
AI111 | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWD.VWFilTms | 0 | AO54 | Dyn Volt-Watt | C: For Function
AI112 | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage measured below the moving average voltage. If the present voltage is above tInverters value, no additional Watts shall be supplied. | 2 | -1000 | 0 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWLo | 0 | AO55 | Dyn Volt-Watt | C: For Function
AI113 | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage measured above the moving average voltage. If the present voltage is below tInverters value, no additional Watts shall be supplied. | 2 | 0 | 1000 | 0.1 | 0 | Percent of nominal voltage | DVWD.DbVWInverter | 0 | AO56 | Dyn Volt-Watt | C: For Function
AI114 | Dynamic Volt-Watt Attempted Output. Watt output that the mode is attempting to achieve based on the Voltage input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DVWD.ReqWSet | 0 |  | Dyn Volt-Watt | C: For Function
AI115 | Frequency-Watt Mode Priority |  | 0 | 100 | 1 | 0 | n/a | DHFW1.ModPrio | 0 | AO57 | Freq-Watt | C: For Function
AI119 | Frequency-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW1.EcpRef | 0 | AO61 | Freq-Watt | C: For Function
AI120 | Frequency-Watt Frequency Reference Input. Frequency measurement read from the meter and used as an input to the mode. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.MMXU.Hz | 0 |  | Freq-Watt | C: For Function
AI121 | Frequency-Watt High Starting Frequency. Delta frequency between start frequency and nominal grid frequency for High frequency events. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | 0 | AO62 | Freq-Watt | C: For Function | M
AI123 | Frequency-Watt High Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | 0 | AO64 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI586 | M
AI124 | Frequency-Watt High Charging Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent frequency difference | DHFW1.WChaGra | 0 | AO65 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI586
AI125 | Frequency-Watt Low Starting Frequency. Delta frequency between start frequency and nominal grid frequency for low frequency events. | 2 | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | 0 | AO66 | Freq-Watt | C: For Function | M
AI127 | Frequency-Watt Low Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | 0 | AO68 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI587 | M
AI128 | Frequency-Watt Low Charging Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent frequency difference | DLFW1.WChaGra | 0 | AO69 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI587
AI131 | Frequency-Watt Ramp Up Time Constant. Time constant or open loop response time for moving from the current active power target to a Higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DLFW1.OplTmsMax.1 | 0 | AO72 | Freq-Watt | C: For Function | M
AI132 | Frequency-Watt Ramp Down Time Constant. Time constant or open loop response time for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | 0 | AO73 | Freq-Watt |  | M
AI142 | Active Power Limit Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWMX.ModPrio | 0 | AO82 | Active Power Limit | C: For Function
AI146 | Active Power Limit Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWMX.EcpRef | 0 | AO86 | Active Power Limit | C: For Function
AI147 | Active Power Limit Reference Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.MMXU.TotW | 0 |  | Active Power Limit | C: For Function
AI148 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | 0 | AO87 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI588 | M
AI149 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | 0 | AO88 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI589 | M
AI150 | Charge/Discharge Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWGC.ModPrio | 0 | AO89 | Set Active Power | C: For Function
AI154 | Charge/Discharge Active Power Target. Percentage of maximum active power. | 2 | -1000 | 1000 | 0.1 | 0 | Percent of WMax | DWGC.GnWPctSpt | 0 | AO93 | Set Active Power | C: For Function if BO46 = 0
AI155 | Charge/Discharge Ramp Up Time Constant. Ramp time, in seconds, for moving from the current active power target to a higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.1 | 0 | AO94 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI156 | Charge/Discharge Ramp Down Time Constant. Ramp time, in seconds, for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWGC.OplTmsMax.2 | 0 | AO95 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI157 | Charge/Discharge Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpuRte | 0 | AO96 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI158 | Charge/Discharge Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpdRteMax | 0 | AO97 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI159 | Charge/Discharge Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpuChaRte | 0 | AO98 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI160 | Charge/Discharge Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWGC.RpdChaRteMax | 0 | AO99 | Set Active Power | C: For Function. Either the time constant or the ramp rate is mandatory.
AI161 | Charge/Discharge Minimum Reserve for Storage. The reserve level below which the storage system may only be discharged in emergency situations, expressed as a percentage of the usable capacity. | 2 | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMinPct | 0 | AO100 | Set Active Power | C: For Storage
AI162 | Charge/Discharge Maximum Reserve for Storage. The reserve level above which the storage system may only be charged in emergency situations, expressed as a percentage of the usable capacity. | 2 | -1000 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DWGC.SocUseMaxPct | 0 | AO101 | Set Active Power | C: For Storage
AI163 | Coordinated Charge/Discharge Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DTCD.ModPrio | 0 | AO102 | Coord Charge-Dischg | C: For Storage
AI167 | Coordinated Charge/Discharge Target State of Charge. Charge that the system is expected to achieve, as a percentage of the usable capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DTCD.SocUseTgtPct | 0 | AO106 | Coord Charge-Dischg | C: For Storage
AI168 | Coordinated Charge/Discharge Target Date. Date by which the storage system must reach the target SOC. Days since January 1, 1970, UTC. | 2 | 0 | 2147483647 | 1 | 0 | Days | DTCD.DateTgt.Date | 0 | AO107 | Coord Charge-Dischg | C: For Storage
AI169 | Coordinated Charge/Discharge Target Time. Time by when the storage system must reach the target SOC. Expressed as the number of seconds since the start of Target Date. | 2 | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.DateTgt.Time | 0 | AO108 | Coord Charge-Dischg | C: For Storage
AI170 | Coordinated Charge/Discharge Energy Request. Amount of energy that must be transferred from the grid to the charger to move the SOC from the value at the specific time of reference to the target SOC. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hours | DTCD.WhReq | 0 | AO109 | Coord Charge-Dischg | C: For Storage
AI171 | Coordinated Charge/Discharge Minimum Charging Duration. Minimum duration to move from the SOC at the time of reference to the target SOC. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurTms | 0 | AO110 | Coord Charge-Dischg | C: For Storage
AI172 | Coordinated Charge/Discharge Date of Reference. Date that the SOC is measured or computed by the storage system and is the basis for the Energy Request, Minimum Charging Duration, and other parameters | 2 | 0 | 2147483647 | 1 | 0 | Days | DTCD.SocDate | 0 | AO111 | Coord Charge-Dischg | C: For Storage
AI173 | Coordinated Charge/Discharge Time of Reference. Time that the SOC is measured or computed by the storage system and is the basis for the Energy Request, Minimum Charging Duration, and other parameters | 2 | 0 | 2147483647 | 1 | 0 | Milliseconds | DTCD.SocDateTms | 0 | AO112 | Coord Charge-Dischg | C: For Storage
AI174 | Coordinated Charge/Discharge Duration at Maximum Charge Rate. Duration that energy can be stored at the Maximum Charge Rate. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.ChaDurMax | 0 | AO113 | Coord Charge-Dischg | C: For Storage
AI175 | Coordinated Charge/Discharge Duration Maximum Discharge Rate. Duration that energy can be delivered at the Maximum Discharge Rate. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DTCD.DschDurMax | 0 | AO114 | Coord Charge-Dischg | C: For Storage
AI176 | Active Power Following Mode #1 (Peak Power Limiting) Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWFL1.ModPrio | 0 | AO115 | Peak Power Limiting | C: For Function
AI180 | Active Power Following Mode #1 (Peak Power Limiting) Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWFL1.EcpRef | 0 | AO119 | Peak Power Limiting | C: For Function
AI181 | Active Power Following Mode #1 (Peak Power Limiting) Reference Power Measured | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.MMXU.TotW | 0 |  | Peak Power Limiting | C: For Function
AI182 | Active Power Following Mode #1 (Peak Power Limiting) Power Threshold | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.FolWThr | 0 | AO120 | Peak Power Limiting | C: For Function
AI183 | Active Power Following Mode #1 (Peak Power Limiting) Ratio. Percent of the power exceeding the Power Threshold | 2 | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL1.FolWPct | 0 | AO121 | Peak Power Limiting | C: For Function
AI184 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpuRte | 0 | AO122 | Peak Power Limiting | C: For Function
AI185 | Active Power Following Mode #1 (Peak Power Limiting) Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL1.RpdRte | 0 | AO123 | Peak Power Limiting | C: For Function
AI186 | Active Power Following Mode #1 (Peak Power Limiting) Attempted Output. Watt output that the mode is attempting to achieve based on the Watts input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL1.ReqW | 0 |  | Peak Power Limiting | C: For Function
AI187 | Active Power Following Mode #2 (Load Following) Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWFL2.ModPrio | 0 | AO124 | Load Following | C: For Function
AI191 | Active Power Following Mode #2 (Load Following) Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWFL2.EcpRef | 0 | AO128 | Load Following | C: For Function
AI192 | Active Power Following Mode #2 (Load Following) Reference Power Measured | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.MMXU.TotW | 0 |  | Load Following | C: For Function
AI193 | Active Power Following Mode #2 (Load Following) Power Threshold | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.FolWThr | 0 | AO129 | Load Following | C: For Function
AI194 | Active Power Following Mode #2 (Load Following) Ratio. Percent of the power exceeding the Power Threshold | 2 | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL2.FolWPct | 0 | AO130 | Load Following | C: For Function
AI195 | Active Power Following Mode #2 (Load Following) Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpuRte | 0 | AO131 | Load Following | C: For Function
AI196 | Active Power Following Mode #2 (Load Following) Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL2.RpdRte | 0 | AO132 | Load Following | C: For Function
AI197 | Active Power Following Mode #2 (Load Following) Attempted Output. Watt output that the mode is attempting to achieve based on the Watts input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL2.ReqW | 0 |  | Load Following | C: For Function
AI198 | Active Power Following Mode #3 (Generation Following) Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWFL3.ModPrio | 0 | AO133 | Generation Following | C: For Function
AI202 | Active Power Following Mode #3 (Generation Following) Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWFL3.EcpRef | 0 | AO137 | Generation Following | C: For Function
AI203 | Active Power Following Mode #3 (Generation Following) Reference Power Measured | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.MMXU.TotW | 0 |  | Generation Following | C: For Function
AI204 | Active Power Following Mode #3 (Generation Following) Power Threshold | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.FolWThr | 0 | AO138 | Generation Following | C: For Function
AI205 | Active Power Following Mode #3 (Generation Following) Ratio. Percent of the power exceeding the Power Threshold | 2 | 0 | 1000 | 0.1 | 0 | Percent of power exceeding threshold | DWFL3.FolWPct | 0 | AO139 | Generation Following | C: For Function
AI206 | Active Power Following Mode #3 (Generation Following) Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpuRte | 0 | AO140 | Generation Following | C: For Function
AI207 | Active Power Following Mode #3 (Generation Following) Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWFL3.RpdRte | 0 | AO141 | Generation Following | C: For Function
AI208 | Active Power Following Mode #3 (Generation Following) Attempted Output. Watt output that the mode is attempting to achieve based on the Watts input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWFL3.ReqW | 0 |  | Generation Following | C: For Function
AI209 | AGC Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DAGC.ModPrio | 0 | AO142 | AGC | C: For Function
AI213 | AGC Active Power Target | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WSpt | 0 | AO146 | AGC | C: For Function
AI214 | AGC Ramp Up Time Constant. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RmpUpTms | 0 | AO147 | AGC | C: For Function
AI215 | AGC Ramp Down Time Constant. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.RmpDnTms | 0 | AO148 | AGC | C: For Function
AI216 | AGC Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpuRte | 0 | AO149 | AGC | C: For Function
AI217 | AGC Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpdRte | 0 | AO150 | AGC | C: For Function
AI218 | AGC Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpuChaRte | 0 | AO151 | AGC | C: For Storage
AI219 | AGC Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DAGC.RpdChaRte | 0 | AO152 | AGC | C: For Storage
AI220 | AGC Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMinPct | 0 | AO153 | AGC | C: For Storage
AI221 | AGC Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocUseMaxPct | 0 | AO154 | AGC | C: For Storage
AI222 | AGC Maximum Watts Available | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WMaxAvl | 0 |  | AGC | C: For Function
AI223 | AGC Minimum Watts Available | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DAGC.WMinAvl | 0 |  | AGC | C: For Function
AI224 | AGC Expected State of Charge | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocExpc | 0 |  | AGC | C: For Function
AI225 | AGC Expected State of Energy | 2 | 0 | 1000 | 0.1 | 0 | Percent | DAGC.SocWhExpc | 0 |  | AGC | C: For Function
AI226 | AGC Expected State of Charge Time Interval | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DAGC.SocExpcTms | 0 |  | AGC | C: For Function
AI227 | Active Power Smoothing Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWSM.ModPrio | 0 | AO155 | Active Power Smoothing | C: For Function
AI231 | Active Power Smoothing Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWSM.EcpRef | 0 | AO159 | Active Power Smoothing | C: For Function
AI232 | Active Power Smoothing Reference Power Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWSM.MMXU.TotW | 0 |  | Active Power Smoothing | C: For Function
AI233 | Active Power Smoothing Gradient. Signed quantity that establishes the ratio of additional smoothing Watts provided to the present delta-watts of the reference load or generation. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Watts per delta-watt | DWSM.WSmthGra | 0 | AO160 | Active Power Smoothing | C: For Function
AI234 | Active Power Smoothing Lower Limit. Difference in Watts from the moving average of the reference power above which no smoothing shall be applied. | 2 | -2147483648 | 0 | 1 | 0 | Watts | DWSM.WSmthLoLim | 0 | AO161 | Active Power Smoothing | C: For Function
AI235 | Active Power Smoothing Upper Limit. Difference in Watts from the moving average of the reference power below which no smoothing shall be applied. | 2 | 0 | 2147483647 | 1 | 0 | Watts | DWSM.WSmthhiLim | 0 | AO162 | Active Power Smoothing | C: For Function
AI236 | Active Power Smoothing Filter Time (Seconds). Time in seconds used to calculate the moving average of the reference load or generation being smoothed. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWSM.FilTms | 0 | AO163 | Active Power Smoothing | C: For Function
AI237 | Active Power Smoothing Discharge Ramp Up Rate. The maximum generation ramp up rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpuRte | 0 | AO164 | Active Power Smoothing | C: For Function
AI238 | Active Power Smoothing Discharge Ramp Down Rate. The maximum generation ramp down rate expressed as a percentage of the Maximum Generation Rate (WMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpdRte | 0 | AO165 | Active Power Smoothing | C: For Function
AI239 | Active Power Smoothing Charge Ramp Up Rate. The maximum charging ramp up rate expressed as a percentage of the Maximum Charging Rate (WChaMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpuChaRte | 0 | AO166 | Active Power Smoothing | C: For Storage
AI240 | Active Power Smoothing Charge Ramp Down Rate. The maximum charging ramp down rate expressed as a percentage of the Maximum Charnging Rate (WChaMax) per second. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DWSM.RpdChaRte | 0 | AO167 | Active Power Smoothing | C: For Storage
AI241 | Active Power Smoothing Attempted Output. Watt output that the mode is attempting to achieve based on the Watt input and other parameters. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWSM.ReqWSet | 0 |  | Active Power Smoothing | C: For Function
AI242 | Volt-Watt Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVWC1.ModPrio | 0 | AO168 | Volt-Watt | C: For Function
AI246 | Volt-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | 0 | AO172 | Volt-Watt | C: For Function | M
AI247 | Volt-Watt Reference Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.MMXN.Vol | 0 |  | Volt-Watt | C: For Function | M
AI248 | Volt-Watt Curve Index. Index of the Volt-Watt curve that should be used by the mode. If zero, then direct paramters are used. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | 0 | AO173 | Volt-Watt | C: For Function | M
AI249 | Volt-Watt Attempted Output. Maximum active power the outstation is permitted to generate or absorb based on the voltage level and gradient. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DVWC1.ReqWLim | 0 |  | Volt-Watt | C: For Function
AI250 | Volt-Watt Filter Time (Seconds) | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.FilTms | 0 | AO174 | Volt-Watt | C: For Function
AI251 | Volt-Watt Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.1 | 0 | AO175 | Volt-Watt | C: For Function
AI252 | Volt-Watt Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVWC1.OplTmsMax.2 | 0 | AO176 | Volt-Watt | C: For Function
AI253 | Volt-Watt Discharging Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuRte | 0 | AO177 | Volt-Watt | C: For Function
AI254 | Volt-Watt Discharging Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdRte | 0 | AO178 | Volt-Watt | C: For Function
AI255 | Volt-Watt Charging Ramp Up Rate. Maximum charging ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuChaRte | 0 | AO179 | Volt-Watt | C: For Function
AI256 | Volt-Watt Charging Ramp Down Rate. Maximum charging ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdChaRte | 0 | AO180 | Volt-Watt | C: For Function
AI257 | Frequency-Watt Curve Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DHFW2.ModPrio | 0 | AO181 | Freq-Watt Curve | C: For Function
AI261 | Frequency-Watt Curve Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.EcpRef | 0 | AO185 | Freq-Watt Curve | C: For Function
AI262 | Frequency-Watt Curve Frequency Reference Input. Frequency measurement read from the meter and used as an input to the mode. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW2.MMXU.Hz | 0 |  | Freq-Watt Curve | C: For Function
AI263 | Frequency-Watt Curve - Curve Index. Index of the Frequency-Watt curve that should be used by the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HzWCrv | 0 | AO186 | Freq-Watt Curve | C: For Function
AI264 | Frequency-Watt Curve - High Frequency Hysteresis Curve Index. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DHFW2.HysCrv | 0 | AO187 | Freq-Watt Curve | C: For Function
AI265 | Frequency-Watt Curve - Low Frequency Hysteresis Curve Index. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DLFW2.HysCrv | 0 | AO188 | Freq-Watt Curve | C: For Function
AI266 | Frequency-Watt Curve Start Delay | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStrDlTmms | 0 | AO189 | Freq-Watt Curve | C: For Function
AI267 | Frequency-Watt Curve Stop Delay | 2 | 0 | 2147483647 | 1 | 0 | milliseconds | DHFW2.ActStopDlTmms | 0 | AO190 | Freq-Watt Curve | C: For Function
AI268 | Frequency-Watt Curve Ramp Up Time Constant. Time constant or open loop response time for moving from the current active power target to a higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.1 | 0 | AO191 | Freq-Watt Curve | C: For Function
AI269 | Frequency-Watt Curve Ramp Down Time Constant. Time constant or open loop response time for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW2.OplTmsMax.2 | 0 | AO192 | Freq-Watt Curve | C: For Function
AI270 | Frequency-Watt Curve Discharge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuRte | 0 | AO193 | Freq-Watt Curve | C: For Function
AI271 | Frequency-Watt Curve Discharge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdRte | 0 | AO194 | Freq-Watt Curve | C: For Function
AI272 | Frequency-Watt Curve Charge Ramp Up Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpuChaRte | 0 | AO195 | Freq-Watt Curve | C: For Storage
AI273 | Frequency-Watt Curve Charge Ramp Down Rate | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DHFW2.RpdChaRte | 0 | AO196 | Freq-Watt Curve | C: For Storage
AI274 | Frequency-Watt Attempted Output. Watt output that the mode is attempting to achieve based on the Frequency input and selected curve. If “Snapshot of Power” is not enabled, this is the maximum active power the outstation will attempt to generate or absorb. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DHFW2.ReqWLim | 0 |  | Freq-Watt Curve | C: For Function
AI275 | Frequency-Watt Curve Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMinPct | 0 | AO197 | Freq-Watt Curve | C: For Storage
AI276 | Frequency-Watt Curve Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent | DHFW2.SocUseMaxPct | 0 | AO198 | Freq-Watt Curve | C: For Storage
AI277 | Constant VArs Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVAR.ModPrio | 0 | AO199 | Const VArs | C: For Function
AI281 | Constant VArs Reactive Power Target. Percentage of maximum reactive power. | 2 | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | 0 | AO203 | Const VArs | C: For Function | M
AI282 | Constant VArs Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.1 | 0 | AO204 | Const VArs | C: For Function
AI283 | Constant VArs Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVAR.OplTmsMax.2 | 0 | AO205 | Const VArs | C: For Function
AI284 | Constant Power Factor Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DFPF.ModPrio | 0 | AO206 | Constant PF | C: For Function
AI288 | Constant Power Factor Setpoint - Generation / Discharging | 2 | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | 0 | AO210 | Constant PF | C: For Function | M
AI289 | Constant Power Factor Setpoint - Charging | 2 | 0 | 100 | 0.01 | 0 | None | DFPF.PFLodTgt | 0 | AO211 | Constant PF | C: For Function
AI290 | Volt-Var Control Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVVR.ModPrio | 0 | AO212 | Volt-VAr | C: For Function
AI294 | Volt-VAr Control Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVVR.EcpRef | 0 | AO216 | Volt-VAr | C: For Function
AI295 | Volt-VAr Control Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVVR.MMXN.Vol | 0 |  | Volt-VAr | C: For Function
AI296 | Volt-VAr Control Adjusted Voltage Reference. The Voltage used as reference for Volt-VAr control. If Autonomous Voltage Reference Adjustment is disabled, this is the same fixed value as the Reference Voltage. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVVR.VRefSet | 0 |  | Volt-VAr | C: For Function
AI297 | Volt-VAr Curve Index. Index of the Volt-VAr curve that should be used by the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVVR.VVArCrv | 0 | AO217 | Volt-VAr | C: For Function
AI298 | Volt-VAr Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.1 | 0 | AO218 | Volt-VAr | C: For Function
AI299 | Volt-VAr Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.OplTmsMax.2 | 0 | AO219 | Volt-VAr | C: For Function
AI300 | Volt-VAr Autonomous Voltage Reference Adjustment Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.VRefTmms | 0 | AO220 | Volt-VAr | C: For Function
AI301 | Volt-VAr Attempted Output. VAr output that the mode is attempting to achieve based on the Voltage input and selected curve. | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DVVR.ReqVAr | 0 |  | Volt-VAr | C: For Function
AI302 | Watt-VAr Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DWVR.ModPrio | 0 | AO221 | Watt-VAr | C: For Function
AI306 | Watt-VAr Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWVR.EcpRef | 0 | AO225 | Watt-VAr | C: For Function
AI307 | Watt-VAr Reference Power Input. Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | Watts | DWVR.MMXU.TotW | 0 |  | Watt-VAr | C: For Function
AI308 | Watt-VAr Curve Index. Index of the Watt-VAr curve that should be used by the mode. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DWVR.WVArCrv | 0 | AO226 | Watt-VAr | C: For Function
AI309 | Watt-VAr Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.1 | 0 | AO227 | Watt-VAr | C: For Function
AI310 | Watt-VAr Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DWVR.OplTmsMax.2 | 0 | AO228 | Watt-VAr | C: For Function
AI311 | Watt-VAr Attempted Output. VAr output that the mode is attempting to achieve based on the Watt input and selected curve. | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DWVR.ReqVAr | 0 |  | Watt-VAr | C: For Function
AI312 | Power Factor Correction Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DPFC.ModPrio | 0 | AO229 | PF Correct | C: For Function
AI316 | Power Factor Correction Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DPFC.EcpRef | 0 | AO233 | PF Correct | C: For Function
AI317 | Power Factor Correction Reference Power Factor Input. Power factor measurement read from the meter and used as an input to the mode. | 2 | -100 | 100 | 0.01 | 0 | None | DFPC.MMXU.TotPF | 0 |  | PF Correct | C: For Function
AI318 | Power Factor Correction Average PF Target | 2 | -100 | 100 | 0.01 | 0 | None | DPFC.PFTrg | 0 | AO234 | PF Correct | C: For Function
AI319 | Power Factor Correction Lower PF Limit | 2 | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.min | 0 | AO235 | PF Correct | C: For Function
AI320 | Power Factor Correction Upper PF Limit | 2 | -100 | 100 | 0.01 | 0 | None | DPFC.PFCorRef.rangeC.max | 0 | AO236 | PF Correct | C: For Function
AI321 | Pricing Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DPRG.ModPrio | 0 | AO237 | Price | C: For Function
AI325 | Pricing Mode Setpoint: Hundredths of local currency per Kilowatt-Hr. | 2 | -2147483648 | 2147483647 | 0.01 | 0 | 100ths of local currency | DPRG.PrcRef | 0 | AO241 | Price | C: For Function
AI326 | Pricing Mode Ramp Up Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.OplTmsMax.1 | 0 | AO242 | Price | C: For Function
AI327 | Pricing Mode Ramp Down Time Constant | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DPRG.OplTmsMax.2 | 0 | AO243 | Price | C: For Function
AI328 | Curve Edit Selector | 2 | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | 1 | AO244 | Curve | M | C: See clause 1.7
AI329 | Curve Type. Enumeration: <0> Curve disabled <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-VAr <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 2 | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | 0 | AO245 | Curve | M | C: See clause 1.7
AI330 | Curve Number of Points | 2 | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | 0 | AO246 | Curve | M | C: See clause 1.7
AI331 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time <29> Voltage <33> Frequency <38> Watts <23> Celsius Temperature <100> Price in hundredths of local currency <129> Voltage as a percent of nominal voltage (VRef) <133> Frequency as a percent of nominal frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | 0 | AO247 | Curve | M | C: See clause 1.7
AI332 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> VArs as percent of max VArs (VARMax) <3> VArs as percent of max available VArs (VArAval) <4> Vars as percent of max apparent Watts (VAMax) - used in IEEE 1547 <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor in EEI notation <8> Volts as a percent of nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage <33> Frequency <38> Watts <99+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | 0 | AO248 | Curve | M | C: See clause 1.7
AI333 | Curve Point 1 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | 0 | AO249 | Curve | M | C: See clause 1.7
AI334 | Curve Point 1 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | 0 | AO250 | Curve | M | C: See clause 1.7
AI335 | Curve Point 2 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | 0 | AO251 | Curve | M | C: See clause 1.7
AI336 | Curve Point 2 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | 0 | AO252 | Curve | M | C: See clause 1.7
AI337 | Curve Point 3 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | 0 | AO253 | Curve | M | C: See clause 1.7
AI338 | Curve Point 3 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | 0 | AO254 | Curve | M | C: See clause 1.7
AI339 | Curve Point 4 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | 0 | AO255 | Curve | M | C: See clause 1.7
AI340 | Curve Point 4 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | 0 | AO256 | Curve | M | C: See clause 1.7
AI341 | Curve Point 5 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.xVal | 0 | AO257 | Curve | M
AI342 | Curve Point 5 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.5.yVal | 0 | AO258 | Curve | M
AI343 | Curve Point 6 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.xVal | 0 | AO259 | Curve | M
AI344 | Curve Point 6 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.6.yVal | 0 | AO260 | Curve | M
AI345 | Curve Point 7 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.xVal | 0 | AO261 | Curve | M
AI346 | Curve Point 7 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.7.yVal | 0 | AO262 | Curve | M
AI347 | Curve Point 8 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.xVal | 0 | AO263 | Curve | M
AI348 | Curve Point 8 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.8.yVal | 0 | AO264 | Curve | M
AI349 | Curve Point 9 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.xVal | 0 | AO265 | Curve | M
AI350 | Curve Point 9 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.9.yVal | 0 | AO266 | Curve | M
AI351 | Curve Point 10 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.xVal | 0 | AO267 | Curve | M
AI352 | Curve Point 10 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.10.yVal | 0 | AO268 | Curve | M
AI533 | System Meter Type of Connection Point. Enumeration: <0> unknown, <1> DER to local EPS <2> Internal to DER <3> local EPS with load to area EPS (PCC with load) <4> local EPS w/o load to area EPS (PCC without load) <5> Load to local EPS <6> External to DER beyond the PCC <7> External to DER within the local EPS <8> Auxiliary DER Load <9> Group of DERs to the area EPS <99> Other | 3 | 0 | 99 | 1 | 0 | Enum | DECP.EcpConnType | 0 |  | Monitoring | M
AI534 | System Meter Type of Circuit Phases. Enumeration: <0> unknown <1> Single phase <2> Split phase <3> 2-phase <4> 3-phase delta <5> 3-phase wye <6> 3-phase wye grounded <7> 3-phase / 3-wire (inverter type) <8> 3-phase / 4-wire (inverter type) | 3 | 0 | 8 | 1 | 0 | Enum | DECP.PhsConnTyp | 0 |  | Monitoring | M
AI535 | System Meter Apparent Power Calculation Method. Calculation method for total apparent power calculation. Enumeration: <0> unknown <1> vector <2> aritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | SYS.MMXU.ClcTotVA | 0 |  | Monitoring | M
AI536 | System Meter Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | SYS.MMXU.Hz | 0 |  | Monitoring | M | M
AI537 | System Meter Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW | 0 |  | Monitoring | M | M
AI538 | System Meter Active Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.W.phsA.mag | 0 |  | Monitoring | M
AI539 | System Meter Active Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.W.phsB.mag | 0 |  | Monitoring | M
AI540 | System Meter Active Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.W.phsC.mag | 0 |  | Monitoring | M
AI541 | System Meter Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | SYS.MMXU.TotVAr | 0 |  | Monitoring | M | M
AI542 | System Meter Reactive Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Var | SYS.MMXU.Var.phsA.mag | 0 |  | Monitoring | M
AI543 | System Meter Reactive Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Var | SYS.MMXU.VAr.phsB.mag | 0 |  | Monitoring | M
AI544 | System Meter Reactive Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Var | SYS.MMXU.VAr.phsC.mag | 0 |  | Monitoring | M
AI545 | System Meter Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | SYS.MMXU.TotPF | 0 |  | Monitoring | M
AI546 | System Meter Apparent Power | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | SYS.MMXU.TotVA | 0 |  | Monitoring | M
AI547 | System Meter Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.mag | 0 |  | Monitoring | M | M
AI548 | System Meter Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsA.ang | 0 |  | Monitoring | M | M
AI549 | System Meter Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.mag | 0 |  | Monitoring | M | M
AI550 | System Meter Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsB.ang | 0 |  | Monitoring | M | M
AI551 | System Meter Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.mag | 0 |  | Monitoring | M | M
AI552 | System Meter Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsC.ang | 0 |  | Monitoring | M | M
AI553 | System Meter Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.AvPPVPhs | 0 |  | Monitoring | M | M
AI554 | System Meter Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsA.mag | 0 |  | Monitoring | M | M
AI555 | System Meter Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsB.mag | 0 |  | Monitoring | M | M
AI556 | System Meter Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsC.mag | 0 |  | Monitoring | M | M
AI557 | System Meter Active Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW.rangeC.hLim | 0 | AO449 | Monitoring | M
AI558 | System Meter Active Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW.rangeC.lLim | 0 | AO450 | Monitoring | M
AI559 | System Meter Reactive Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | var | SYS.MMXU.TotVAr.rangeC.hLim | 0 | AO451 | Monitoring | M
AI560 | System Meter Reactive Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | var | SYS.MMXU.TotVAr.rangeC.lLim | 0 | AO452 | Monitoring | M
AI561 | System Meter Power Factor – High Threshold | 3 | -100 | 100 | 0.01 | 0 | None | SYS.MMXU.TotPF.rangeC.hLim | 0 | AO453 | Monitoring | M
AI562 | System Meter Power Factor – Low Threshold | 3 | -100 | 100 | 0.01 | 0 | None | SYS.MMXU.TotPF.rangeC.lLim | 0 | AO454 | Monitoring | M
AI563 | System Meter Phase A Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.rangeC.hLim | 0 | AO455 | Monitoring | M
AI564 | System Meter Phase A Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.rangeC.lLim | 0 | AO456 | Monitoring | M
AI565 | System Meter Phase B Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.rangeC.hLim | 0 | AO457 | Monitoring | M
AI566 | System Meter Phase B Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.rangeC.lLim | 0 | AO458 | Monitoring | M
AI567 | System Meter Phase C Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.rangeC.hLim | 0 | AO459 | Monitoring | M
AI568 | System Meter Phase C Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.rangeC.lLim | 0 | AO460 | Monitoring | M
AI590 | Frequency-Watt Droop High Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | 0 | AO480 | Droop Freq-Watt | C: For Function | M
AI591 | Frequency-Watt Droop Low Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | 0 | AO481 | Droop Freq-Watt | C: For Function | M
AI592 | High Frequency-Watt Droop Minimum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | 0 | AO482 | Droop Freq-Watt | C: For Function | M
AI593 | Low Frequency-Watt Droop Maximum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | 0 | AO483 | Droop Freq-Watt | C: For Function | M
AI618 | Charge/Discharge. Watts instead of percent WMax | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWGC.GnWSpt | 0 | AO508 | Charge/Discharge | C: For Function If BI114=1
AI619 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | 0 | AO509 | Active Power Limit | C: For Function if BI113 = 1 | M
AI620 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | 0 | AO510 | Active Power Limit | C: For Function if BI113 = 1 | M
AI621 | Constant Vars using vars as unit | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | 0 | AO511 | Constant Vars | C: For Function if BI115 = 1 | M
AI2000 | Running Schedule Index | 2 | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCC.ActSchdRef | 0 |  | BC Scheduling | C: For Back Comp
AI2001 | Schedule to Edit Selector (n) | 3 | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCC.Schd | 0 | AO2000 | BC Scheduling | C: For Back Comp
AI2002 | Selected Schedule Identity | 3 | 0 | 2147483647 | 1 | 0 | n/a | BC.FSCCn.Schd | 0 | AO2001 | BC Scheduling | C: For Back Comp
AI2003 | Selected Schedule Priority | 3 | 1 | 2147483647 | 1 | 0 | n/a | BC.FSCHn.SchdPrio | 1 | AO2002 | BC Scheduling | C: For Back Comp
AI2004 | Selected Schedule Type. Enumeration: <1> Low/High Voltage Ride-Through – hi Must Trip <2> Low/High Voltage Ride-Through – Low Must Trip <3> Low/High Voltage Ride-Through – hi Momentary <4> Low/High Voltage Ride-Through – Lo Momentary <5> Low/High Frequency Ride-Through – hi Must Trip <6> Low/High Frequency Ride-Through – Lo Must Trip <7> Low/High Frequency Ride-Through – hi Momentary <8> Low/High Frequency Ride-Through – Low Momentary <9> Dynamic Reactive Current Support - On/Off <10> Dynamic Volt-Watt - On/Off <11> Frequency-Watt - On/Off <12> Active Power Limit - Charging <13> Active Power Limit - Discharging <14> Charge/Discharge - Percent of Maximum <15> Coordinated Charge/Discharge - SOC Target <16> Active Power Response #1 - On/Off <17> Active Power Response #2 - On/Off <18> Active Power Response #3 - On/Off <19> AGC – Watts <20> Active Power Smoothing - On/Off <21> Volt-Watt – Curve Index <22> Frequency-Watt Curve – Curve Index <23> Frequency-Watt Curve – High Hysteresis <24> Frequency-Watt Curve – Low Hysteresis <25> Constant VArs - Percent of Maximum <26> Constant Power Factor - Power Factor <27> Volt-VAr – Curve Index <28> Watt-VAr – Curve Index <29> Power Factor Correction - On/Off <30> Reserved - For pricing mode <31> Charge/Discharge - enable/disable <32> Coordinated Charge/Discharge - enable/disable <33> Active Power Limit - Discharging - enable/disable <34> Active Power Response #1 - Limit <35> Active Power Response #2 - Limit <36> Active Power Response #3 - Limit <37> AGC - enable/disable ... <100> Vendor-specific enumerations above | 3 | 0 | 50 | 1 | 0 | Enum | MESAn.SchdTyp | 0 | AO2003 | BC Scheduling | C: For Back Comp
AI2005 | Selected Schedule Start Date | 3 | 0 | 2147483647 | 1 | 0 | Days | BC.FSCHn.StrTm.Date | 0 | AO2004 | BC Scheduling | C: For Back Comp
AI2006 | Selected Schedule Start Time | 3 | 0 | 86400000 | 1 | 0 | Seconds | BC.FSCHn.StrTm.Time | 0 | AO2005 | BC Scheduling | C: For Back Comp
AI2007 | Selected Schedule Repeat Interval | 3 | 0 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.NxtStrTm | 0 | AO2006 | BC Scheduling | C: For Back Comp
AI2008 | Selected Schedule Repeat Interval Units | 3 | 0 | 8 | 1 | 0 | n/a | BC.FSCHn.SchdReuse | 0 | AO2007 | BC Scheduling | C: For Back Comp
AI2009 | Selected Schedule Validation Status | 3 | 0 | 5 | 1 | 0 | n/a | BC.FSCHn.SchdSt.1 | 0 |  | BC Scheduling | C: For Back Comp
AI2010 | Selected Schedule Status | 2 | 0 | 5 | 1 | 0 | Enum | BC.FSCHn.SchdSt.2 | 0 |  | BC Scheduling | C: For Back Comp
AI2011 | Selected Schedule Number of Points | 3 | 0 | 2147483647 | 1 | 0 | Integer | BC.FSCHn.NumEntr | 20 | AO2008 | BC Scheduling | C: For Back Comp
AI2012 | Selected Schedule Point [1] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.1 | 0 | AO2009 | BC Scheduling | C: For Back Comp
AI2013 | Selected Schedule Point [1] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.1 | 0 | AO2010 | BC Scheduling | C: For Back Comp
AI2014 | Selected Schedule Point [2] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.2 | 0 | AO2011 | BC Scheduling | C: For Back Comp
AI2015 | Selected Schedule Point [2] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.2 | 0 | AO2012 | BC Scheduling | C: For Back Comp
AI2016 | Selected Schedule Point [3] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.3 | 0 | AO2013 | BC Scheduling | C: For Back Comp
AI2017 | Selected Schedule Point [3] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.3 | 0 | AO2014 | BC Scheduling | C: For Back Comp
AI2018 | Selected Schedule Point [4] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.4 | 0 | AO2015 | BC Scheduling | C: For Back Comp
AI2019 | Selected Schedule Point [4] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.4 | 0 | AO2016 | BC Scheduling | C: For Back Comp
AI2020 | Selected Schedule Point [5] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.5 | 0 | AO2017 | BC Scheduling | C: For Back Comp
AI2021 | Selected Schedule Point [5] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.5 | 0 | AO2018 | BC Scheduling | C: For Back Comp
AI2022 | Selected Schedule Point [6] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.6 | 0 | AO2019 | BC Scheduling | C: For Back Comp
AI2023 | Selected Schedule Point [6] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.6 | 0 | AO2020 | BC Scheduling | C: For Back Comp
AI2024 | Selected Schedule Point [7] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.7 | 0 | AO2021 | BC Scheduling | C: For Back Comp
AI2025 | Selected Schedule Point [7] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.7 | 0 | AO2022 | BC Scheduling | C: For Back Comp
AI2026 | Selected Schedule Point [8] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.8 | 0 | AO2023 | BC Scheduling | C: For Back Comp
AI2027 | Selected Schedule Point [8] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.8 | 0 | AO2024 | BC Scheduling | C: For Back Comp
AI2028 | Selected Schedule Point [9] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.9 | 0 | AO2025 | BC Scheduling | C: For Back Comp
AI2029 | Selected Schedule Point [9] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.9 | 0 | AO2026 | BC Scheduling | C: For Back Comp
AI2030 | Selected Schedule Point [10] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.10 | 0 | AO2027 | BC Scheduling | C: For Back Comp
AI2031 | Selected Schedule Point [10] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.10 | 0 | AO2028 | BC Scheduling | C: For Back Comp
AI2032 | Selected Schedule Point [11] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.11 | 0 | AO2029 | BC Scheduling | C: For Back Comp
AI2033 | Selected Schedule Point [11] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.11 | 0 | AO2030 | BC Scheduling | C: For Back Comp
AI2034 | Selected Schedule Point [12] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.12 | 0 | AO2031 | BC Scheduling | C: For Back Comp
AI2035 | Selected Schedule Point [12] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.12 | 0 | AO2032 | BC Scheduling | C: For Back Comp
AI2036 | Selected Schedule Point [13] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.13 | 0 | AO2033 | BC Scheduling | C: For Back Comp
AI2037 | Selected Schedule Point [13] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.13 | 0 | AO2034 | BC Scheduling | C: For Back Comp
AI2038 | Selected Schedule Point [14] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.14 | 0 | AO2035 | BC Scheduling | C: For Back Comp
AI2039 | Selected Schedule Point [14] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.14 | 0 | AO2036 | BC Scheduling | C: For Back Comp
AI2040 | Selected Schedule Point [15] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.15 | 0 | AO2037 | BC Scheduling | C: For Back Comp
AI2041 | Selected Schedule Point [15] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.15 | 0 | AO2038 | BC Scheduling | C: For Back Comp
AI2042 | Selected Schedule Point [16] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.16 | 0 | AO2039 | BC Scheduling | C: For Back Comp
AI2043 | Selected Schedule Point [16] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.16 | 0 | AO2040 | BC Scheduling | C: For Back Comp
AI2044 | Selected Schedule Point [17] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.17 | 0 | AO2041 | BC Scheduling | C: For Back Comp
AI2045 | Selected Schedule Point [17] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.17 | 0 | AO2042 | BC Scheduling | C: For Back Comp
AI2046 | Selected Schedule Point [18] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.18 | 0 | AO2043 | BC Scheduling | C: For Back Comp
AI2047 | Selected Schedule Point [18] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.18 | 0 | AO2044 | BC Scheduling | C: For Back Comp
AI2048 | Selected Schedule Point [19] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.19 | 0 | AO2045 | BC Scheduling | C: For Back Comp
AI2049 | Selected Schedule Point [19] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.19 | 0 | AO2046 | BC Scheduling | C: For Back Comp
AI2050 | Selected Schedule Point [20] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | BC.FSCHn.SchdIntv.20 | 0 | AO2047 | BC Scheduling | C: For Back Comp
AI2051 | Selected Schedule Point [20] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | BC.FSCHn.SchdEntr.20 | 0 | AO2048 | BC Scheduling | C: For Back Comp
AI2300 | Schedule [1] Status Editing = 1; Validated = 2; Enabled = 3; Running = 4; | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH1.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2301 | Schedule [1] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH1.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2302 | Schedule [1] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH1.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2303 | Schedule [2] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH2.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2304 | Schedule [2] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH2.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2305 | Schedule [2] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH2.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2306 | Schedule [3] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH3.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2307 | Schedule [3] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH3.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2308 | Schedule [3] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH3.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2309 | Schedule [4] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH4.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2310 | Schedule [4] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH4.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2311 | Schedule [4] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH4.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2312 | Schedule [5] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH5.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2313 | Schedule [5] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH5.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2314 | Schedule [5] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH5.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2315 | Schedule [6] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH6.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2316 | Schedule [6] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH6.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2317 | Schedule [6] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH6.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2318 | Schedule [7] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH7.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2319 | Schedule [7] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH7.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2320 | Schedule [7] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH7.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2321 | Schedule [8] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH8.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2322 | Schedule [8] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH8.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2323 | Schedule [8] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH8.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2324 | Schedule [9] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH9.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2325 | Schedule [9] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH9.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2326 | Schedule [9] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH9.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2327 | Schedule [10] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH10.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2328 | Schedule [10] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH10.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2329 | Schedule [10] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH10.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2330 | Schedule [11] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH11.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2331 | Schedule [11] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH11.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2332 | Schedule [11] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH11.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2333 | Schedule [12] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH12.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2334 | Schedule [12] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH12.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2335 | Schedule [12] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH12.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2336 | Schedule [13] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH13.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2337 | Schedule [13] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH13.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2338 | Schedule [13] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH13.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2339 | Schedule [14] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH14.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2340 | Schedule [14] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH14.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2341 | Schedule [14] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH14.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2342 | Schedule [15] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH15.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2343 | Schedule [15] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH15.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2344 | Schedule [15] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH15.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2345 | Schedule [16] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH16.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2346 | Schedule [16] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH16.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2347 | Schedule [16] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH16.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2348 | Schedule [17] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH17.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2349 | Schedule [17] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH17.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2350 | Schedule [17] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH17.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2351 | Schedule [18] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH18.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2352 | Schedule [18] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH18.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2353 | Schedule [18] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH18.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2354 | Schedule [19] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH19.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2355 | Schedule [19] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH19.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2356 | Schedule [19] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH19.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI2357 | Schedule [20] Status | 2 | 0 | 4 | 1 | 0 | Enum | BC.FSCH20.SchdSt | 0 |  | BC Scheduling | C: For Back Comp
AI2358 | Schedule [20] Priority | 2 | 1 | 100 | 1 | 0 | n/a | BC.FSCH20.SchdPrio | 1 |  | BC Scheduling | C: For Back Comp
AI2359 | Schedule [20] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | BC.FSCH20.ActStrTm | 0 |  | BC Scheduling | C: For Back Comp
AI3000 | Schedule to Edit Selector (n) | 3 | 0 | 2147483647 | 1 | 0 | n/a | FSCC.Schd | 0 | AO3000 | Scheduling | C: For Sched
AI3001 | Selected Schedule Identity | 3 | 0 | 2147483647 | 1 | 0 | n/a | FSCCn.Schd | 0 | AO3001 | Scheduling | C: For Sched
AI3002 | Selected Schedule Priority | 3 | 1 | 2147483647 | 1 | 0 | n/a | FSCHn.SchdPrio | 1 | AO3002 | Scheduling | C: For Sched
AI3003 | Selected Schedule Start Date | 3 | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | 0 | AO3003 | Scheduling | C: For Sched
AI3004 | Selected Schedule Start Time | 3 | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | 0 | AO3004 | Scheduling | C: For Sched
AI3005 | Selected Schedule Stop Date | 3 | 0 | 2147483647 | 1 | 0 | Days | FSCHn.StrTm.Date | 0 | AO3005 | Scheduling | C: For Sched
AI3006 | Selected Schedule Stop Time | 3 | 0 | 86400000 | 1 | 0 | Seconds | FSCHn.StrTm.Time | 0 | AO3006 | Scheduling | C: For Sched
AI3007 | Selected Schedule Repeat Interval | 3 | 0 | 2147483647 | 1 | 0 | Varies | FSCHn.NxtStrTm | 0 | AO3007 | Scheduling | C: For Sched
AI3008 | Selected Schedule Repeat Interval Units | 3 | 0 | 8 | 1 | 0 | n/a | FSCHn.SchdReuse | 0 | AO3008 | Scheduling | C: For Sched
AI3009 | Selected Schedule Validation State | 3 | 0 | 7 | 1 | 0 | n/a | FSCHn.SchdSt.1 | 0 |  | Scheduling | C: For Sched
AI3010 | Selected Schedule Status | 2 | 0 | 7 | 1 | 0 | Enum | FSCHn.SchdSt.2 | 0 |  | Scheduling | C: For Sched
AI3011 | Selected Schedule Number of Points | 3 | 0 | 2147483647 | 1 | 0 | Integer | FSCHn.NumEntr | 20 | AO3009 | Scheduling | C: For Sched
AI3012 | Selected Schedule Point [1] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.1 | 0 | AO3010 | Scheduling | C: For Sched
AI3013 | Selected Schedule Point [1] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.1 | 0 | AO3011 | Scheduling | C: For Sched
AI3014 | Selected Schedule Point [1] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.1 | 0 | AO3012 | Scheduling | C: For Sched
AI3015 | Selected Schedule Point [1] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.1 | 1 | AO3013 | Scheduling | C: For Sched
AI3016 | Selected Schedule Point [2] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.2 | 0 | AO3014 | Scheduling | C: For Sched
AI3017 | Selected Schedule Point [2] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.2 | 0 | AO3015 | Scheduling | C: For Sched
AI3018 | Selected Schedule Point [2] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.2 | 0 | AO3016 | Scheduling | C: For Sched
AI3019 | Selected Schedule Point [2] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.2 | 0 | AO3017 | Scheduling | C: For Sched
AI3020 | Selected Schedule Point [3] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.3 | 0 | AO3018 | Scheduling | C: For Sched
AI3021 | Selected Schedule Point [3] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.3 | 0 | AO3019 | Scheduling | C: For Sched
AI3022 | Selected Schedule Point [3] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.3 | 0 | AO3020 | Scheduling | C: For Sched
AI3023 | Selected Schedule Point [3] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.3 | 0 | AO3021 | Scheduling | C: For Sched
AI3024 | Selected Schedule Point [4] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.4 | 0 | AO3022 | Scheduling | C: For Sched
AI3025 | Selected Schedule Point [4] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.4 | 0 | AO3023 | Scheduling | C: For Sched
AI3026 | Selected Schedule Point [4] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.4 | 0 | AO3024 | Scheduling | C: For Sched
AI3027 | Selected Schedule Point [4] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.4 | 0 | AO3025 | Scheduling | C: For Sched
AI3028 | Selected Schedule Point [5] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.5 | 0 | AO3026 | Scheduling | C: For Sched
AI3029 | Selected Schedule Point [5] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.5 | 0 | AO3027 | Scheduling | C: For Sched
AI3030 | Selected Schedule Point [5] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.5 | 0 | AO3028 | Scheduling | C: For Sched
AI3031 | Selected Schedule Point [5] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.5 | 0 | AO3029 | Scheduling | C: For Sched
AI3032 | Selected Schedule Point [6] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.6 | 0 | AO3030 | Scheduling | C: For Sched
AI3033 | Selected Schedule Point [6] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.6 | 0 | AO3031 | Scheduling | C: For Sched
AI3034 | Selected Schedule Point [6] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.6 | 0 | AO3032 | Scheduling | C: For Sched
AI3035 | Selected Schedule Point [6] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.6 | 0 | AO3033 | Scheduling | C: For Sched
AI3036 | Selected Schedule Point [7] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.7 | 0 | AO3034 | Scheduling | C: For Sched
AI3037 | Selected Schedule Point [7] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.7 | 0 | AO3035 | Scheduling | C: For Sched
AI3038 | Selected Schedule Point [7] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.7 | 0 | AO3036 | Scheduling | C: For Sched
AI3039 | Selected Schedule Point [7] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.7 | 0 | AO3037 | Scheduling | C: For Sched
AI3040 | Selected Schedule Point [8] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.8 | 0 | AO3038 | Scheduling | C: For Sched
AI3041 | Selected Schedule Point [8] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.8 | 0 | AO3039 | Scheduling | C: For Sched
AI3042 | Selected Schedule Point [8] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.8 | 0 | AO3040 | Scheduling | C: For Sched
AI3043 | Selected Schedule Point [8] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.8 | 0 | AO3041 | Scheduling | C: For Sched
AI3044 | Selected Schedule Point [9] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.9 | 0 | AO3042 | Scheduling | C: For Sched
AI3045 | Selected Schedule Point [9] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.9 | 0 | AO3043 | Scheduling | C: For Sched
AI3046 | Selected Schedule Point [9] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.9 | 0 | AO3044 | Scheduling | C: For Sched
AI3047 | Selected Schedule Point [9] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.9 | 0 | AO3045 | Scheduling | C: For Sched
AI3048 | Selected Schedule Point [10] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.10 | 0 | AO3046 | Scheduling | C: For Sched
AI3049 | Selected Schedule Point [10] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.10 | 0 | AO3047 | Scheduling | C: For Sched
AI3050 | Selected Schedule Point [10] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.10 | 0 | AO3048 | Scheduling | C: For Sched
AI3051 | Selected Schedule Point [10] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.10 | 0 | AO3049 | Scheduling | C: For Sched
AI3052 | Selected Schedule Point [11] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.11 | 0 | AO3050 | Scheduling | C: For Sched
AI3053 | Selected Schedule Point [11] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.11 | 0 | AO3051 | Scheduling | C: For Sched
AI3054 | Selected Schedule Point [11] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.11 | 0 | AO3052 | Scheduling | C: For Sched
AI3055 | Selected Schedule Point [11] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.11 | 0 | AO3053 | Scheduling | C: For Sched
AI3056 | Selected Schedule Point [12] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.12 | 0 | AO3054 | Scheduling | C: For Sched
AI3057 | Selected Schedule Point [12] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.12 | 0 | AO3055 | Scheduling | C: For Sched
AI3058 | Selected Schedule Point [12] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.12 | 0 | AO3056 | Scheduling | C: For Sched
AI3059 | Selected Schedule Point [12] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.12 | 0 | AO3057 | Scheduling | C: For Sched
AI3060 | Selected Schedule Point [13] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.13 | 0 | AO3058 | Scheduling | C: For Sched
AI3061 | Selected Schedule Point [13] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.13 | 0 | AO3059 | Scheduling | C: For Sched
AI3062 | Selected Schedule Point [13] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.13 | 0 | AO3060 | Scheduling | C: For Sched
AI3063 | Selected Schedule Point [13] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.13 | 0 | AO3061 | Scheduling | C: For Sched
AI3064 | Selected Schedule Point [14] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.14 | 0 | AO3062 | Scheduling | C: For Sched
AI3065 | Selected Schedule Point [14] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.14 | 0 | AO3063 | Scheduling | C: For Sched
AI3066 | Selected Schedule Point [14] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.14 | 0 | AO3064 | Scheduling | C: For Sched
AI3067 | Selected Schedule Point [14] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.14 | 0 | AO3065 | Scheduling | C: For Sched
AI3068 | Selected Schedule Point [15] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.15 | 0 | AO3066 | Scheduling | C: For Sched
AI3069 | Selected Schedule Point [15] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.15 | 0 | AO3067 | Scheduling | C: For Sched
AI3070 | Selected Schedule Point [15] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.15 | 0 | AO3068 | Scheduling | C: For Sched
AI3071 | Selected Schedule Point [15] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.15 | 0 | AO3069 | Scheduling | C: For Sched
AI3072 | Selected Schedule Point [16] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.16 | 0 | AO3070 | Scheduling | C: For Sched
AI3073 | Selected Schedule Point [16] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.16 | 0 | AO3071 | Scheduling | C: For Sched
AI3074 | Selected Schedule Point [16] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.16 | 0 | AO3072 | Scheduling | C: For Sched
AI3075 | Selected Schedule Point [16] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.16 | 0 | AO3073 | Scheduling | C: For Sched
AI3076 | Selected Schedule Point [17] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.17 | 0 | AO3074 | Scheduling | C: For Sched
AI3077 | Selected Schedule Point [17] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.17 | 0 | AO3075 | Scheduling | C: For Sched
AI3078 | Selected Schedule Point [17] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.17 | 0 | AO3076 | Scheduling | C: For Sched
AI3079 | Selected Schedule Point [17] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.17 | 0 | AO3077 | Scheduling | C: For Sched
AI3080 | Selected Schedule Point [18] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.18 | 0 | AO3078 | Scheduling | C: For Sched
AI3081 | Selected Schedule Point [18] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.18 | 0 | AO3079 | Scheduling | C: For Sched
AI3082 | Selected Schedule Point [18] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.18 | 0 | AO3080 | Scheduling | C: For Sched
AI3083 | Selected Schedule Point [18] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.18 | 0 | AO3081 | Scheduling | C: For Sched
AI3084 | Selected Schedule Point [19] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.19 | 0 | AO3082 | Scheduling | C: For Sched
AI3085 | Selected Schedule Point [19] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.19 | 0 | AO3083 | Scheduling | C: For Sched
AI3086 | Selected Schedule Point [19] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.19 | 0 | AO3084 | Scheduling | C: For Sched
AI3087 | Selected Schedule Point [19] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.19 | 0 | AO3085 | Scheduling | C: For Sched
AI3088 | Selected Schedule Point [20] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | Seconds | FSCHn.SchdIntv.20 | 0 | AO3086 | Scheduling | C: For Sched
AI3089 | Selected Schedule Point [20] Action Type | 2 | 0 | 2 | 1 | 0 | Integer | Type.FSCHn.SchdEntr.20 | 0 | AO3087 | Scheduling | C: For Sched
AI3090 | Selected Schedule Point [20] Action Index | 2 | 0 | 64999 | 1 | 0 | Point Index | Point.FSCHn.SchdEntr.20 | 0 | AO3088 | Scheduling | C: For Sched
AI3091 | Selected Schedule Point [20] Value | 2 | -2147483648 | 2147483647 | 1 | 0 | Varies | FSCHn.ValMV.20 | 0 | AO3089 | Scheduling | C: For Sched
AI3500 | Schedule [1] Status Editing = 1; Submitted = 2; Validated = 3; Enabled = 4; Running = 5; Running but not Active = 6, Cycle Completed = 7; Completed and Expired = 8; Disabled = 9; Invalid = 10; Error = 11 | 2 | 0 | 11 | 1 | 0 | Enum | FSCH1.SchdSt | 0 |  | Scheduling | C: For Sched
AI3501 | Schedule [1] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH1.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3502 | Schedule [1] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH1.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3503 | Schedule [2] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH2.SchdSt | 0 |  | Scheduling | C: For Sched
AI3504 | Schedule [2] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH2.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3505 | Schedule [2] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH2.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3506 | Schedule [3] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH3.SchdSt | 0 |  | Scheduling | C: For Sched
AI3507 | Schedule [3] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH3.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3508 | Schedule [3] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH3.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3509 | Schedule [4] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH4.SchdSt | 0 |  | Scheduling | C: For Sched
AI3510 | Schedule [4] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH4.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3511 | Schedule [4] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH4.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3512 | Schedule [5] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH5.SchdSt | 0 |  | Scheduling | C: For Sched
AI3513 | Schedule [5] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH5.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3514 | Schedule [5] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH5.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3515 | Schedule [6] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH6.SchdSt | 0 |  | Scheduling | C: For Sched
AI3516 | Schedule [6] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH6.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3517 | Schedule [6] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH6.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3518 | Schedule [7] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH7.SchdSt | 0 |  | Scheduling | C: For Sched
AI3519 | Schedule [7] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH7.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3520 | Schedule [7] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH7.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3521 | Schedule [8] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH8.SchdSt | 0 |  | Scheduling | C: For Sched
AI3522 | Schedule [8] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH8.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3523 | Schedule [8] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH8.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3524 | Schedule [9] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH9.SchdSt | 0 |  | Scheduling | C: For Sched
AI3525 | Schedule [9] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH9.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3526 | Schedule [9] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH9.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3527 | Schedule [10] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH10.SchdSt | 0 |  | Scheduling | C: For Sched
AI3528 | Schedule [10] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH10.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3529 | Schedule [10] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH10.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3530 | Schedule [11] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH11.SchdSt | 0 |  | Scheduling | C: For Sched
AI3531 | Schedule [11] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH11.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3532 | Schedule [11] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH11.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3533 | Schedule [12] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH12.SchdSt | 0 |  | Scheduling | C: For Sched
AI3534 | Schedule [12] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH12.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3535 | Schedule [12] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH12.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3536 | Schedule [13] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH13.SchdSt | 0 |  | Scheduling | C: For Sched
AI3537 | Schedule [13] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH13.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3538 | Schedule [13] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH13.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3539 | Schedule [14] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH14.SchdSt | 0 |  | Scheduling | C: For Sched
AI3540 | Schedule [14] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH14.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3541 | Schedule [14] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH14.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3542 | Schedule [15] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH15.SchdSt | 0 |  | Scheduling | C: For Sched
AI3543 | Schedule [15] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH15.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3544 | Schedule [15] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH15.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3545 | Schedule [16] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH16.SchdSt | 0 |  | Scheduling | C: For Sched
AI3546 | Schedule [16] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH16.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3547 | Schedule [16] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH16.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3548 | Schedule [17] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH17.SchdSt | 0 |  | Scheduling | C: For Sched
AI3549 | Schedule [17] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH17.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3550 | Schedule [17] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH17.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3551 | Schedule [18] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH18.SchdSt | 0 |  | Scheduling | C: For Sched
AI3552 | Schedule [18] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH18.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3553 | Schedule [18] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH18.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3554 | Schedule [19] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH19.SchdSt | 0 |  | Scheduling | C: For Sched
AI3555 | Schedule [19] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH19.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3556 | Schedule [19] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH19.ActStrTm | 0 |  | Scheduling | C: For Sched
AI3557 | Schedule [20] Status | 2 | 0 | 11 | 1 | 0 | Enum | FSCH20.SchdSt | 0 |  | Scheduling | C: For Sched
AI3558 | Schedule [20] Priority | 2 | 1 | 100 | 1 | 0 | n/a | FSCH20.SchdPrio | 1 |  | Scheduling | C: For Sched
AI3559 | Schedule [20] Active Step Number | 2 | 0 | 100 | 1 | 0 | n/a | FSCH20.ActStrTm | 0 |  | Scheduling | C: For Sched
AI5000 | Meter #1 Type of Connection Point | 3 | 0 | 99 | 1 | 0 | Enum | Meter1.DECP.EcpConnType | 0 |  | Equipment Data
AI5001 | Meter #1 DER Input/Output Included. <0> unknown <1> metered value does not include input/output of the DER <2> metered value includes all input/output of the DER <3> other | 3 | 0 | 3 | 1 | 0 | Enum | Meter1.DECP.DERMsIncl | 0 |  | Equipment Data
AI5002 | Meter #1 Type of Circuit Phases. <0> unknown <1> Single phase <2> Split phase <3> 2-phase <4> 3-phase delta <5> 3-phase wye <6> 3-phase wye grounded <7> 3-phase / 3-wire (inverter type) <8> 3-phase / 4-wire (inverter type) | 3 | 0 | 8 | 1 | 0 | Enum | Meter1.DECP.PhsConnTyp | 0 |  | Equipment Data
AI5003 | Meter #1 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Meter1.MMXU.ClcTotVA | 0 |  | Equipment Data
AI5004 | Meter #1 Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | Meter1.MMXU.Hz | 0 |  | Equipment Data
AI5005 | Meter #1 Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW | 0 |  | Equipment Data
AI5006 | Meter #1 Active Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsA.mag | 0 |  | Equipment Data
AI5007 | Meter #1 Active Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsB.mag | 0 |  | Equipment Data
AI5008 | Meter #1 Active Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.W.phsC.mag | 0 |  | Equipment Data
AI5009 | Meter #1 Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr | 0 |  | Equipment Data
AI5010 | Meter #1 Reactive Power A | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsA.mag | 0 |  | Equipment Data
AI5011 | Meter #1 Reactive Power B | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsB.mag | 0 |  | Equipment Data
AI5012 | Meter #1 Reactive Power C | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.VAr.phsC.mag | 0 |  | Equipment Data
AI5013 | Meter #1 Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF | 0 |  | Equipment Data
AI5014 | Meter #1 Apparent Power | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | Meter1.MMXU.TotVA | 0 |  | Equipment Data
AI5015 | Meter #1 Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.mag | 0 |  | Equipment Data
AI5016 | Meter #1 Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsA.ang | 0 |  | Equipment Data
AI5017 | Meter #1 Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.mag | 0 |  | Equipment Data
AI5018 | Meter #1 Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsB.ang | 0 |  | Equipment Data
AI5019 | Meter #1 Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.mag | 0 |  | Equipment Data
AI5020 | Meter #1 Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | Meter1.MMXU.PhV.phsC.ang | 0 |  | Equipment Data
AI5021 | Meter #1 Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.AvPPVPhs | 0 |  | Equipment Data
AI5022 | Meter #1 Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsA.mag | 0 |  | Equipment Data
AI5023 | Meter #1 Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsB.mag | 0 |  | Equipment Data
AI5024 | Meter #1 Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Meter1.MMXU.A.phsC.mag | 0 |  | Equipment Data
AI5025 | Meter #1 Active Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.hLim | 0 | AO5000 | Equipment Data
AI5026 | Meter #1 Active Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Watts | Meter1.MMXU.TotW.rangeC.lLim | 0 | AO5001 | Equipment Data
AI5027 | Meter #1 Reactive Power – High Threshold | 3 | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.hLim | 0 | AO5002 | Equipment Data
AI5028 | Meter #1 Reactive Power – Low Threshold | 3 | 0 | 2147483647 | 1 | 0 | Vars | Meter1.MMXU.TotVAr.rangeC.lLim | 0 | AO5003 | Equipment Data
AI5029 | Meter #1 Power Factor – High Threshold | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.hLim | 0 | AO5004 | Equipment Data
AI5030 | Meter #1 Power Factor – Low Threshold | 3 | -100 | 100 | 0.01 | 0 | None | Meter1.MMXU.TotPF.rangeC.lLim | 0 | AO5005 | Equipment Data
AI5031 | Meter #1 Phase A Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.hLim | 0 | AO5006 | Equipment Data
AI5032 | Meter #1 Phase A Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsA.rangeC.lLim | 0 | AO5007 | Equipment Data
AI5033 | Meter #1 Phase B Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.hLim | 0 | AO5008 | Equipment Data
AI5034 | Meter #1 Phase B Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsB.rangeC.lLim | 0 | AO5009 | Equipment Data
AI5035 | Meter #1 Phase C Volts – High Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.hLim | 0 | AO5010 | Equipment Data
AI5036 | Meter #1 Phase C Volts – Low Threshold | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Meter1.MMXU.PhV.phsC.rangeC.lLim | 0 | AO5011 | Equipment Data
AI10000 | DER Unit #1 Unit Type. Enumeration: <0> unknown <1> Diesel / gas engine <2> Gas Turbine engine <3> PV <4> PV plus Storage <5> Lithium Ion Battery Storage <6> Fuel cell <7> Hydro generator <8> Wind turbine <9> Flow battery storage <10> Air compression storage <11> Flywheel storage <12> Capacitor storage <13> Vehicle-to-Grid (V2G) <50> Mixed, hybrid DER <98> Not applicable / Unknown <99> Other | 3 | 0 | 99 | 1 | 0 | Enum | DER_Unit1.DGEN.DERTyp | 0 |  | Equipment Data
AI10001 | DER Unit #1 Nameplate Energy Capacity. Nameplate energy capacity for the DER unit expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DER_Unit1.DGEN.WMeteraxRtg | 0 |  | Equipment Data
AI10002 | IEEE 1547 Normal Operating Performance Category. <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DER_Unit1.DGEN.RegCls.1 | 0 |  | Equipment Data
AI10003 | IEEE 1547 Abnormal Operating Performance Category. <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DER_Unit1.DGEN.RegCls.2 | 0 |  | Equipment Data
AI10004 | DER Unit #1 Maximum Apparent Generation Power | 2 | 0 | 2147483647 | 1 | 0 | VA | DER_Unit1.DGEN.VAMax | 0 |  | Equipment Data
AI10005 | DER Unit #1 Maximum Apparent Charging Power | 2 | -2147483648 | 0 | 1 | 0 | VA | DER_Unit1.DSTO.ChaVAMax | 0 |  | Equipment Data
AI10006 | DER Unit #1 Operational Time. Time in seconds since commissioning. | 3 | 0 | 2147483647 | 1 | 0 | Seconds | DER_Unit1.DGEN.GnOpTms | 0 |  | Equipment Data
AI10007 | DER Unit #1 Connection Time. Number of hours the DER unit has been connected to the power system. | 3 | 0 | 2147483647 | 1 | 0 | Hours | DER_Unit1.DGEN.OpTmRs | 0 |  | Equipment Data
AI10008 | DER Unit #1 Available Active Generation Power | 1 | 0 | 2147483647 | 1 | 0 | W | DER_Unit1.DSTO.WAvlUp | 0 |  | Equipment Data
AI10009 | DER Unit #1 Available Active Charging Power | 1 | -2147483648 | 0 | 1 | 0 | W | DER_Unit1.DSTO.WAvlDn | 0 |  | Equipment Data
AI10010 | DER Unit #1 Available Reactive Injection Power | 1 | 0 | 2147483647 | 1 | 0 | Vars | DER_Unit1.DGEN.TotIvarAvl | 0 |  | Equipment Data
AI10011 | DER Unit #1 Available Reactive Absorption Power | 1 | -2147483648 | 0 | 1 | 0 | Vars | DER_Unit1.DGEN.TotAvarAvl | 0 |  | Equipment Data
AI10012 | DER Unit #1 Non-impacting Injection VArs Available. VArs that can be injected without impacting Active Power Output | 2 | 0 | 2147483647 | 1 | 0 | Vars | DER_Unit1.DGEN.IvarAvl | 0 |  | Equipment Data
AI10013 | DER Unit #1 Non-impacting Absorption VArs Available. VArs that can be absorbed without impacting Active Power Output | 2 | -2147483648 | 0 | 1 | 0 | Vars | DER_Unit1.DGEN.AvarAvl | 0 |  | Equipment Data
AI10014 | DER Unit #1 Link to Meter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | DER_Unit1.MESA.MeterNum | 0 |  | Equipment Data
AI15000 | Inverter #1 Apparent Power Calculation Method. <0> Reserved <1> Vector <2> AritMeteretic | 2 | 0 | 2 | 1 | 0 | Enum | Inverter1.MMXU.ClcTotVA | 0 |  | Equipment Data
AI15001 | Inverter #1 Active Power Target | 1 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter1.DINV.WTgt | 0 |  | Equipment Data
AI15002 | Inverter #1 Reactive Power Target | 1 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter1.DINV.VArTgtPct | 0 |  | Equipment Data
AI15003 | Inverter #1 Active Power. Present active power measurement. | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW | 0 |  | Equipment Data
AI15004 | Inverter #1 Reactive Power. Present reactive power measurement. | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr | 0 |  | Equipment Data
AI15005 | Inverter #1 Power Factor | 2 | -100 | 100 | 0.01 | 0 | None | Inverter1.MMXU.TotPF | 0 |  | Equipment Data
AI15006 | Inverter #1 Apparent Power | 2 | -2147483648 | 2147483647 | 1 | 0 | VA | Inverter1.MMXU.TotVA | 0 |  | Equipment Data
AI15007 | Inverter #1 DC Input Power | 3 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt | 0 |  | Equipment Data
AI15008 | Inverter #1 DC Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol | 0 |  | Equipment Data
AI15009 | Inverter #1 DC Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp | 0 |  | Equipment Data
AI15010 | Inverter #1 Average Line to Neutral Voltage. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PhV | 0 |  | Equipment Data
AI15011 | Inverter #1 Voltage Phase A to B. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsAB | 0 |  | Equipment Data
AI15012 | Inverter #1 Voltage Phase B to C. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsBC | 0 |  | Equipment Data
AI15013 | Inverter #1 Voltage Phase C to A. AC voltage measurement. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMXU.PPV.phsCA | 0 |  | Equipment Data
AI15014 | Inverter #1 AC Current. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A | 0 |  | Equipment Data
AI15015 | Inverter #1 Current Phase A. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsA | 0 |  | Equipment Data
AI15016 | Inverter #1 Current Phase B. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsB | 0 |  | Equipment Data
AI15017 | Inverter #1 Current Phase C. AC current measurement. | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMXU.A.phsC | 0 |  | Equipment Data
AI15018 | Inverter #1 Internal (Cabinet) Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.EnclTmp | 0 |  | Equipment Data
AI15019 | Inverter #1 Heat Sink Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.HeatSinkTmp | 0 |  | Equipment Data
AI15020 | Inverter #1 Transformer Temperature | 2 | -200 | 200 | 0.1 | 0 | Deg C | Inverter1.DINV.TrfTmp | 0 |  | Equipment Data
AI15021 | Inverter #1 Active Power Output - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.hLim | 0 | AO15000 | Equipment Data
AI15022 | Inverter #1 Active Power Output - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMXU.TotW.RangeC.lLim | 0 | AO15001 | Equipment Data
AI15023 | Inverter #1 Reactive Power Output – High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.hLim | 0 | AO15002 | Equipment Data
AI15024 | Inverter #1 Reactive Power Output – Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Vars | Inverter1.MMXU.TotVAr.rangeC.lLim | 0 | AO15003 | Equipment Data
AI15025 | Inverter #1 Current Output Frequency – High Threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.hLim | 0 | AO15004 | Equipment Data
AI15026 | Inverter #1 Current Output Frequency – Low Threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | Inverter1.MMXU.Hz.rangeC.lLim | 0 | AO15005 | Equipment Data
AI15027 | Inverter #1 DC Inverter Input Power - High Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.hLim | 0 | AO15006 | Equipment Data
AI15028 | Inverter #1 DC Inverter Input Power - Low Threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | Inverter1.MMDC.Watt.RangeC.lLim | 0 | AO15007 | Equipment Data
AI15029 | Inverter #1 DC Current Available – High Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp.RangeC.hLim | 0 | AO15008 | Equipment Data
AI15030 | Inverter #1 DC Current Available – Low Threshold | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Inverter1.MMDC.Amp.RangeC.lLim | 0 | AO15009 | Equipment Data
AI15031 | Inverter #1 DC Voltage Between DER System and Inverter – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.hLim | 0 | AO15010 | Equipment Data
AI15032 | Inverter #1 DC Voltage Between DER System and Inverter – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Inverter1.MMDC.Vol.RangeC.lLim | 0 | AO15011 | Equipment Data
AI15033 | Inverter #1 Link to DER Unit # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Inverter1.MESA.DER_UnitNum | 0 |  | Equipment Data
AI20000 | Battery Bank #1 Type of Storage. <0> n/a, Unknown <1> Lead-acid <2> Nickel-metal hydrate (NiMH) <3> Nickel-cadmium (NiCad) <4> LitInverterum <5> Carbon zinc <6> Zinc chloride <7> Alkaline <8> Rechargeable alkaline <9> Sodium sulphur (NaS) <10> Flow <99> Other | 2 | 0 | 99 | 1 | 0 | Enum | Battery1.DBAT.BatTyp | 0 |  | Equipment Data
AI20001 | Battery Bank #1 Nameplate Actual Capacity Rating. The actual total capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery1.DBAT.WMeteraxRtg | 0 |  | Equipment Data
AI20002 | Battery Bank #1 Effective Capacity. The present effective capacity of the battery bank expressed in Storage Capacity Units. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs or Amp-hrs | Battery1.DBAT.EffWh | 0 |  | Equipment Data
AI20003 | Battery Bank #1 Minimum Reserve for Storage. As a percentage of the nominal useable storage (DBAT.CapWhUseRtg) | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.UseWMeterinPct | 0 |  | Equipment Data
AI20004 | Battery Bank #1 Maximum Reserve for Storage. As a percentage of the nominal useable storage (DBAT.CapWhUseRtg). Expressed as a delta from the maximum usable capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.UseWMeteraxPct | 0 |  | Equipment Data
AI20005 | Battery Bank #1 Battery State. <0> n/a, Unknown <1> Disconnected <2> Initializing <3> Connected <4> Standby <5> SOC Protection <6> Suspending <99> Fault | 2 | 0 | 99 | 1 | 0 | Enum | Battery1.DBAT.BatSt | 0 |  | Equipment Data
AI20006 | Battery Bank #1 Actual State of Charge. Currently available energy in the battery, as a percentage of the effective capacity. | 3 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.SocWh | 0 |  | Equipment Data
AI20007 | Battery Bank #1 State of Health. The ratio (expressed as a percentage) of the current rating of the battery with respect to the nameplate rating of the battery and end-of-life criteria. The rating of the battery may include one or more battery parameters that are selected as appropriate for the application and implementation. These parameters often include the energy capacity, but could also incorporate other measurements. | 1 | 0 | 1000 | 0.1 | 0 | Percent | Battery1.DBAT.EffWhPct | 0 |  | Equipment Data
AI20008 | Battery Bank #1 External Battery Voltage. Voltage measured between battery charger and battery. | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVol | 0 |  | Equipment Data
AI20009 | Battery Bank #1 Internal Battery Voltage. Internal voltage measurement. | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVol | 0 |  | Equipment Data
AI20010 | Battery Bank #1 Current | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | Battery1.DBAT.Amp | 0 |  | Equipment Data
AI20011 | Battery Bank #1 Power | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Watts | Battery1.DBAT.Watt | 0 |  | Equipment Data
AI20012 | Battery Bank #1 Minimum Cell Voltage. Minimum cell voltage measurement of all cells in the bank. | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery1.SBAT.CelVolLo | 0 |  | Equipment Data
AI20013 | Battery Bank #1 Maximum Cell Voltage. Maximum cell voltage measurement of all cells in the bank. | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | Battery1.SBAT.CelVolInverter | 0 |  | Equipment Data
AI20014 | Battery Bank #1 Minimum Temperature. Minimum temperature measurement for all sensors in the bank. | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.SBAT.CelTmpMin | 0 |  | Equipment Data
AI20015 | Battery Bank #1 Maximum Temperature. Maximum temperature measurement for all sensors in the bank. | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.SBAT.CelTmpMax | 0 |  | Equipment Data
AI20016 | Battery Bank #1 External Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.DBAT.ExtTmp | 0 |  | Equipment Data
AI20017 | Battery Bank #1 Internal Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | Battery1.DBAT.IntnTmp | 0 |  | Equipment Data
AI20018 | Battery Bank #1 Charge Current Limit. Instantaneous current limit on charging. | 1 | -2147483648 | 0 | 0.1 | 0 | Amps | Battery1.DBAT.ChaAmpLim | 0 |  | Equipment Data
AI20019 | Battery Bank #1 Discharge Current Limit. Instantaneous current limit on discharging. | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | Battery1.DBAT.DschAmpLim | 0 |  | Equipment Data
AI20020 | Battery Bank #1 Minimum Voltage Limit. Instantaneous minimum voltage limit. | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.VolMinLim | 0 |  | Equipment Data
AI20021 | Battery Bank #1 Maximum Voltage Limit. Instantaneous maximum voltage limit. | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.VolMaxLim | 0 |  | Equipment Data
AI20022 | Battery Bank #1 Connected String Count. Number of strings in the bank that are currently connected. | 1 | 0 | 2147483647 | 1 | 0 | n/a | Battery1.DBAT.CelStrgCnt | 0 |  | Equipment Data
AI20023 | Battery Bank #1 External Voltage - High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolInverterAls | 0 | AO20000 | Equipment Data
AI20024 | Battery Bank #1 External Voltage - Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.ExtVolLoAls | 0 | AO20001 | Equipment Data
AI20025 | Battery Bank #1 Internal Voltage – High Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolInverterAls | 0 | AO20002 | Equipment Data
AI20026 | Battery Bank #1 Internal Voltage – Low Threshold | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | Battery1.DBAT.IntnVolLoAls | 0 | AO20003 | Equipment Data
AI20027 | Battery Bank #1 Link to Inverter # | 2 | 0 | 2147483647 | 1 | 0 | n/a | Battery1.MESA.InverterNum | 0 |  | Equipment Data
AI30000 | Volt-Watt Adv Mode Priority | 2 | 0 | 100 | 1 | 0 | n/a | DVWC1.ModPrio | 0 | AO30000 | Volt-Watt Advanced | C: For Function
AI30004 | Volt-Watt Adv Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | 0 | AO30004 | Volt-Watt Advanced | C: For Function
AI30005 | Volt-Watt Adv Reference Voltage Input. Voltage measurement read from the signal meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.MMXN.Vol | 0 |  | Volt-Watt Advanced | C: For Function
AI30006 | Volt-Watt Adv High Start Voltage Threshold. Voltage threshold for starting high voltage events. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | 0 | AO30005 | Volt-Watt Advanced | C: For Function
AI30008 | Volt-Watt Adv Low Start Voltage Threshold. Voltage threshold for starting low voltage events. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.HzStr | 0 | AO30007 | Volt-Watt Advanced | C: For Function
AI30012 | Volt-Watt Adv Curve Index. Index of the Volt-Watt Adv curve that should be used by the m | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | 0 | AO30011 | Volt-Watt Advanced | C: For Function
AI30013 | Volt-Watt Adv Attempted Output. Maximum active power the outstation is permitted to generate or absorb based on the voltage level and gradient. | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DVWC1.ReqWLim | 0 |  | Volt-Watt Advanced | C: For Function
AI30017 | Volt-Watt Adv Discharging Ramp Up Rate. Maximum ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuRte | 0 | AO30015 | Volt-Watt Advanced | C: For Function
AI30018 | Volt-Watt Adv Discharging Ramp Down Rate. Maximum ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdRte | 0 | AO30016 | Volt-Watt Advanced | C: For Function
AI30019 | Volt-Watt Adv Charging Ramp Up Rate. Maximum charging ramp up rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpuChaRte | 0 | AO30017 | Volt-Watt Advanced | C: For Function
AI30020 | Volt-Watt Adv Charging Ramp Down Rate. Maximum charging ramp down rate. | 2 | 0 | 500000 | 0.1 | 0 | Percent per Second | DVWC1.RpdChaRte | 0 | AO30018 | Volt-Watt Advanced | C: For Function
AI30021 | Volt-Watt Adv Minimum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMinPct | 0 | AO30019 | Volt-Watt Advanced | C: For Function
AI30022 | Volt-Watt Adv Maximum Usable SOC | 2 | 0 | 1000 | 0.1 | 0 | Percent of maximum usable SOC | DVWC1.SocUseMaxPct | 0 | AO30020 | Volt-Watt Advanced | C: For Function
AI30054 | Synthetic Inertia Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DSYN.EcpRef | 0 | AO30054 | Synthetic Inertia | C: For Function
AI30055 | Set the Synthetic Inertia Discharge Ramp Up Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.DschRpuPct | 0 | AO30055 | Synthetic Inertia | C: For Function
AI30056 | Set the Synthetic Inertia Discharge Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.DschRpdPct | 0 | AO30056 | Synthetic Inertia | C: For Function
AI30057 | Set the Synthetic Inertia Charge Ramp Up Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.ChaRpuPct | 0 | AO30057 | Synthetic Inertia | C: For Function
AI30058 | Set the Synthetic Inertia Charge Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Percent per Second | DSYN.ChaRpdPct | 0 | AO30058 | Synthetic Inertia | C: For Function
AI30059 | Set the Synthetic Inertia Derivative Factor | 2 | 0 | 2147483647 | 1 | 0 | Percent W per Hz per sec | DSYN.RcfWHzTmPct | 0 | AO30059 | Synthetic Inertia | C: For Function
AI30060 | Set the Synthetic Inertia Lower Deadband | 2 | 0 | 2147483647 | 1 | 0 | Hz | DSYN.DbHzMin | 0 | AO30060 | Synthetic Inertia | C: For Function
AI30061 | Set the Synthetic Inertia Upper Deadband | 2 | 0 | 2147483647 | 1 | 0 | Hz | DSYN.DbHzMax | 0 | AO30061 | Synthetic Inertia | C: For Function

## CTR
DNP3 Point Index | Name / Description | Default Class Assigned to Counter Events | Frozen Counter Exists (Yes or No) | Default Class Assigned to Frozen Counter Events | IEC 61850 | Additional Information |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Purpose/Mode/ Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
CTR5000 | Meter #1 Active Energy Delivered. Measured in watt-hours. | n/a | Yes | 3 | HM1MMTR.SupWh | Metering
CTR5001 | Meter #1 Active Energy Received. Measured in watt-hours. | n/a | Yes | 3 | HM1MMTR.DmdWh | Metering
CTR5002 | Meter #1 Reactive Energy Delivered. Measured in VAr-hours. | n/a | Yes | 3 | HM1MMTR.SupVArh | Metering
CTR5003 | Meter #1 Reactive Energy Received. Measured in VAr-hours. | n/a | Yes | 3 | HM1MMTR.DmdVArh | Metering

## System Diagrams
Naming of Data Objects