## Key
IEEE 1815.2 Standard Profile Companion Data Point Tables: Version 1.1
DNP3 Points |  | Start Index | BO | BI | AO | AI | CTR
SCADA
Configuration & Control Points |  | 0 | 0 | 0 | 0 | 0 | 0
Functions |  | 0 | 12 | 31 | 22 | 71 | 0 |  | Configuration Settings
Curves | Max of 100 x,y pairs per Curve | 0 | 0 | 107 | 244 | 328 | 0 |  | Allocate the number of curves and the maximum number of points per curve
System Meter |  | 0 | 0 | 94 | 449 | 533 | 0
Extensions beyond DNP3 AN2018-001 |  | 0 | 42 | 108 | 461 | 569 | 0
Gap #1 | Reserved for future extensions | x | 44 | 111 | 476 | 586
Schedules
Schedules (2 items/step) | Time offset, value (for backwards compat) | 2000 | 2000 | 2000 | 2000 | 2000 |  |  | Allocate number of schedules and the maximum points per schedule
Schedule Status (2 items) | Schedule Status of first 100 | 2300 |  | 2300 |  | 2300
Schedules (4 items/step) | Time offset, Action type, AO or BO Index, & Value | 3000 | 3000 | 3000 | 3000 | 3000
Schedule Status (4 items) | Schedule Status of first 100 | 3500 | - | 3500 | - | 3500
Gap #2 | Reserved for future extensions | 4000
Equipment Points |  |  | BO | BI | AO | AI | CTR | Enter Maximum # of Devices
Meters | Start of additional meter points | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | No. of Meters
| mh(1) set of points per meter |  | 0 | 13 | 12 | 37 | 4
| mh(n) total length of points |  | 0 | 39 | 36 | 111 | 12
DER Units | Start of DER unit points. | 10000 | 10000 | 10000 | 10000 | 10000 |  | 0 | No. DER Units
| duh(1) set of points per DER unit |  | 0 | 4 | 0 | 15 | 0
| duh(n) total length of points |  | 0 | 28 | 0 | 98
Inverters | Start of inverter points. | 15000 | 15000 | 15000 | 15000 | 15000 |  | 0 | No. Inverters
| ihh(1) set of points per inverter |  | 0 | 35 | 12 | 34 | 0
| ihh(n) total length of points |  | 0 | 70 | 24 | 66
Batteries | Start of battery points. | 20000 | 20000 | 20000 | 20000 | 20000 |  | 0 | No. Batteries
| bhh(1) set of points per battery |  | 0 | 54 | 4 | 28 | 0 | For each meter, DER unit, inverter, and battery, additional historical data rows need to be added in the spreadsheet to define the actual points
| bhh(n) total length of points |  | 0 | 108 | 8 | 54
Experimental Extensions | Reserved for experimental extensions | 30000
Vendor Points (VP) |  | 50000 | 50000 | 50000 | 50000 | 50000 |  | State if Storage
Start Index Points | Used for optional Auto Discovery | 60000 |  |  |  | 60000 |  | Yes | Storage? Yes or No
Maximum Index Value |  | 65535
mhbi(n) | Starting index of meter #n binary inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhbi(n) | Starting index of DER unit #n binary inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihbi(n) | Starting index of inverter #n binary inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhbi(n) | Starting index of battery #n binary inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhai(n) | Starting index of meter #n analog inputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
duhai(n) | Starting index of DER unit #n analog inputs relative to HDU. |  |  | 1 <= n <= Number of DER units (u)
ihai(n) | Starting index of inverter #n analog inputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhai(n) | Starting index of battery #n analog inputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)
mhao(n) | Starting index of meter #n analog outputs relative to HM. |  |  | 1 <= n <= Number of meters (m)
ihao(n) | Starting index of inverter #n analog outputs relative to HI. |  |  | 1 <= n <= Number of inverters (i)
bhao(n) | Starting index of battery #n analog outputs relative to HB. |  |  | 1 <= n <= Number of batteries (b)

## BO
DNP3 Point Index | Name / Description | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  |  |  | IEC61850UniqueString | Assoc. BI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BO3 | System Permission to Start | Start Permission Not Granted | Start Permission Granted | DGEN.PrmConn | BI16 | Enter Service | M | M
BO17 | Enable Active Power Limit Mode | Disable | Enable | DWMX.Mod | BI69 | Active Power Limit | C: For Function | M
BO25 | Enable Volt-Watt Mode | Disable | Enable | DVWC.Mod | BI77 | Volt-Watt | C: For Function | M
BO27 | Enable Constant Vars Mode | Disable | Enable | DVAR.Mod | BI79 | Const Vars | C: For Function | M
BO28 | Enable Constant Power Factor Mode | Disable | Enable | DFPF.Mod | BI80 | Constant PF | C: For Function | M
BO29 | Enable Volt-Var Control Mode | Disable | Enable | DVVR.Mod | BI81 | Volt-Var | C: For Function | M
BO41 | Volt-Var Enable Autonomous Voltage Reference Adjustment | Disable | Enable | DVVR.VRefAdjEna | BI93 | Volt-Var | C: For Function | M

## BI
DNP3 Point Index | Name / Description | Default Event Class | Name for State when value is 0 | Name for State when value is 1 | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Assoc. BO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)
BI0 | System Communication Error | 1 | Normal | Alarm: Communications error exists in the ESS | LCCH1.ChLiv |  | Alarm | M | M
BI1 | System Has Priority 1 Alarms | 1 | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH.GrAlm |  | Alarm | M | M
BI21 | DER is Off but Available to Start | 2 | Null | Off-Available | DGEN.DEROpSt.disconnectedandavailable |  | Monitoring | M | M
BI22 | DER is Off and Not Available to Start | 2 | Null | Off-Not-Available | DGEN.DEROpSt.disconnectedandblocked |  | Monitoring | M | M
BI31 | Supports Low/High Voltage Ride-Through Mode | 0 | Not Supported | Supported | DHVT |  | Volt Ride-Through | M | M
BI32 | Supports Low/High Frequency Ride-Through Mode | 0 | Not Supported | Supported | DHFT |  | Freq Ride-Through | M | M
BI35 | Supports Frequency-Watt Mode | 0 | Not Supported | Supported | DHFW |  | Freq-Watt | M | M
BI36 | Supports Active Power Limit Mode | 0 | Not Supported | Supported | DWMX |  | Active Power Limit | M | M
BI44 | Supports Volt-Watt Mode | 0 | Not Supported | Supported | DVWC |  | Volt-Watt | M | M
BI46 | Supports Constant VArs Mode | 0 | Not Supported | Supported | DVAR |  | Const Vars | M | M
BI47 | Supports Constant Power Factor Mode | 0 | Not Supported | Supported | DFPF |  | Constant PF | M | M
BI48 | Supports Volt-VAr Control Mode | 0 | Not Supported | Supported | DVVR |  | Volt-Var | M | M
BI49 | Supports Watt-VAr Mode | 0 | Not Supported | Supported | DWVR |  | Watt-Var | M | M
BI69 | Operating Mode - Active Power Limit Enabled | 2 | Disabled | Enabled | DWMX.Mod | BO17 | Active Power Limit | C: For Function | M
BI77 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWC.Mod | BO25 | Volt-Watt | C: For Function | M
BI79 | Operating Mode - Constant VArs Enabled | 2 | Disabled | Enabled | DVAR.Mod | BO27 | Const Vars | C: For Function | M
BI80 | Operating Mode - Constant Power Factor Enabled | 2 | Disabled | Enabled | DFPF.Mod | BO28 | Constant PF | C: For Function | M
BI81 | Operating Mode - Volt-VAR Control Enabled | 2 | Disabled | Enabled | DVVR.Mod | BO29 | Volt-Var | C: For Function | M
BI82 | Operating Mode - Watt-VAr Enabled | 2 | Disabled | Enabled | DWVR.Mod | BO30 | Watt-Var | C: For Function | M

## AO
DNP3 Point Index | Name / Description | Transmitted Value |  | Scaling |  | Units | IEC 61850 | Additional Information |  |  |  | EUT Capabilities
|  | Minimum | Maximum | Multiplier | OffSet |  | IEC61850UniqueString | Assoc. AI | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AO23 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV1.BlkRef | AI73 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO24 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV1.BlkRef | AI74 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO25 | Low/High Voltage Ride-Through High Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHVT.PTOV2.BlkRef | AI75 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO26 | Low/High Voltage Ride-Through Low Momentary Cessation Curve Index. Index of the Voltage Ride-through curve which specifies where generation/discharging must stop when the voltage is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLVT.PTUV2.BlkRef | AI76 | Volt Ride-Through | C: For Function, unless set at implementation | M
AO28 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is high. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DHFT.PTOF1.BlkRef | AI79 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO29 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. A zero (0) values means the curve is not used. | 0 | 2147483647 | 1 | 0 | n/a | DLFT.PTUF1.BlkRef | AI80 | Freq Ride-Through | C: For Function, unless set at implementation | M
AO62 | Frequency-Watt High Starting Frequency | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | AI121 | Freq-Watt | C: For Function | M
AO64 | Frequency-Watt High Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | AI123 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO476 | M
AO66 | Frequency-Watt Low Starting Frequency | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | AI125 | Freq-Watt | C: For Function | M
AO68 | Frequency-Watt Low Discharging / Generating Gradient | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | AI127 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AO477 | M
AO72 | Frequency-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.1 | AI131 | Freq-Watt |  | M
AO73 | Frequency-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | AI132 | Freq-Watt |  | M
AO87 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | AI148 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO478 | M
AO88 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | AI149 | Active Power Limit | C: For Function or if BO45 set to Watts Type, use AO479 | M
AO173 | Volt-Watt Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVWC.VWCrv | AI248 | Volt-Watt | C: For Function, unless set at implementation as zero | C: See clause 1.7
AO175 | Volt-Watt Ramp Up Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.1 | AI251 | Volt-Watt | C: For Function | M
AO176 | Volt-Watt Ramp Down Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVWC.OplTmsMax.2 | AI252 | Volt-Watt | C: For Function | M
AO203 | Constant Vars Reactive Power Target | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | AI281 | Const Vars | C: For Function | M
AO210 | Constant Power Factor Setpoint - Generation/Discharging | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | AI288 | Constant PF | C: For Function | M
AO211 | Constant Power Factor Setpoint - Charging | 0 | 100 | 0.01 | 0 | None | DFPF.PFLodTgt | AI289 | Constant PF | C: For Function | M
AO217 | Volt-Var Curve Index | 0 | 2147483647 | 1 | 0 | n/a | DVVR.VVArCrv | AI297 | Volt-Var | C: For Function | M
AO220 | Volt-Var Autonomous Voltage Reference Adjustment Time Constant | 0 | 2147483647 | 1 | 0 | Seconds | DVVR.VRefTmms | AI300 | Volt-Var | C: For Function | M
AO244 | Curve Edit Selector. Writing to this point selects which of the curves can currently be viewed and changed. | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | AI328 | Curve | C: See clause 1.7 | C: See clause 1.7

## AI
DNP3 Point Index | Name / Description | Default Event Class | Transmitted Value |  | Scaling |  | Units | IEC61850 | Additional Information |  |  |  |  | EUT Capabilities
|  |  | Minimum | Maximum | Multiplier | Offset |  | IEC61850UniqueString | Value | Assoc. AO | Purpose/Mode/Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”) | EUT Minimum? >= Minimum | EUT Maximum? <= Maximum
AI2 | Nameplate Minimum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMinRtg | 0 |  | Nameplate | M | M
AI3 | Nameplate Maximum Voltage Rating | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | DGEN.VMaxRtg | 0 |  | Nameplate | M | M
AI4 | Nameplate Active Generation Power Rating at Unity Power Factor | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMaxRtg | 0 |  | Nameplate | M | M
AI6 | Nameplate Active Generation Power Rating at Specified Over-Excited Power Factor, injecting reactive power (as positive vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WOvPFRtg | 0 |  | Nameplate | M | M
AI8 | Specified Over-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.OvPFRtg | 0 |  | Nameplate | M | M
AI9 | Nameplate Active Generation Power Rating at Specified Under-Excited Power Factor, absorbing reactive power (as negative vars) | 3 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WUnPFRtg | 0 |  | Nameplate | M | M
AI10 | Nameplate Active Charging Power Rating at Specified Under-Excited Power Factor | 3 | -2147483648 | 0 | 1 | 0 | Watts | DSTO.ChaWUnPFRtg | 0 |  | Nameplate | M | M
AI11 | Specified Under-Excited Power Factor | 3 | -100 | 100 | 0.01 | 0 | None | DGEN.UnPFRtg | 0 |  | Nameplate | M | M
AI12 | Nameplate Reactive Supply (Injection) Power Rating | 3 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMaxRtg | 0 |  | Nameplate | M | M
AI13 | Nameplate Reactive Absorption Power Rating | 3 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMaxRtg | 0 |  | Nameplate | M | M
AI15 | Nameplate Apparent Charging Power Rating | 3 | -2147483648 | 0 | 1 | 0 | VAs | DSTO.ChaVAMaxRtg | 0 |  | Nameplate | M | M
AI16 | Nameplate Storage Actual Energy Capacity. Nameplate (original) actual total energy capacity of the storage system expressed in Storage Capacity Units. | 3 | 0 | 2147483647 | 1 | 0 | Amp-hrs or Watt-hrs | DSTO.WhRtg | 0 |  | Nameplate | C: For Storage | M
AI21 | Remaining Reactive Susceptance | 3 | -2147483648 | 2147483647 | 1 | 0 | Siemens | DGEN.SuscRtg | 0 |  | Nameplate |  | M
AI22 | IEEE 1547 Normal Operating Performance Category. Enumeration: <0> unknown <1> Category A <2> Category B | 3 | 0 | 2 | 1 | 0 | Enum | DGEN.RegClas.1 | 0 |  | Nameplate | M | M
AI23 | IEEE 1547 Abnormal Operating Performance Category. Enumeration: <0> unknown <1> Category I <2> Category II <3> Category III | 3 | 0 | 3 | 1 | 0 | Enum | DGEN.RegClas.2 | 0 |  | Nameplate | M | M
AI29 | Reference Voltage | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DECP.VRef | 0 | AO0 | Config | M | M
AI30 | Reference Voltage Offset | 2 | -2147483648 | 2147483647 | 0.1 | 0 | Volts | DECP.VRefOfs | 0 | AO1 | Config | M | M
AI32 | Maximum Active Generation Power | 2 | 0 | 2147483647 | 1 | 0 | Watts | DGEN.WMax | 0 |  | Operational Settings | M | M
AI34 | Maximum Reactive Injection Power | 2 | 0 | 2147483647 | 1 | 0 | Vars | DGEN.IvarMax | 0 |  | Operational Settings | M | M
AI35 | Maximum Reactive Absorption Power | 2 | -2147483648 | 0 | 1 | 0 | Vars | DGEN.AvarMax | 0 |  | Operational Settings | M | M
AI48 | System Usable State of Charge. Present usable energy in the DER as a percentage of Nameplate Storage Usable Capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | DSTO.UseSocPct | 0 |  | Monitoring | C: For Storage | M
AI121 | Frequency-Watt High Starting Frequency. Delta frequency between start frequency and nominal grid frequency for High frequency events. | 2 | 0 | 70000 | 0.001 | 0 | Hz | DHFW1.HzStr | 0 | AO62 | Freq-Watt | C: For Function | M
AI123 | Frequency-Watt High Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DHFW1.WGra | 0 | AO64 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI586 | M
AI125 | Frequency-Watt Low Starting Frequency. Delta frequency between start frequency and nominal grid frequency for low frequency events. | 2 | -70000 | 0 | 0.001 | 0 | Hz | DLFW1.HzStr | 0 | AO66 | Freq-Watt | C: For Function | M
AI127 | Frequency-Watt Low Discharging / Generating Gradient | 2 | -2147483648 | 2147483647 | 0.001 | 0 | Percent watts per percent Hz difference | DLFW1.WGra | 0 | AO68 | Freq-Watt | C: For Function or if BO44 set to Enabled, use AI587 | M
AI131 | Frequency-Watt Ramp Up Time Constant. Time constant or open loop response time for moving from the current active power target to a Higher active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DLFW1.OplTmsMax.1 | 0 | AO72 | Freq-Watt | C: For Function | M
AI132 | Frequency-Watt Ramp Down Time Constant. Time constant or open loop response time for moving from the current active power target to a lower active power target. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | DHFW1.OplTmsMax.2 | 0 | AO73 | Freq-Watt |  | M
AI148 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMX.WLimPct | 0 | AO87 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI588 | M
AI149 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | 0 | 1000 | 0.1 | 0 | Percent of WMax | DWMN.WLimPct | 0 | AO88 | Active Power Limit | C: For Function or if BI113 set to Enabled, use AI589 | M
AI246 | Volt-Watt Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.EcpRef | 0 | AO172 | Volt-Watt | C: For Function | M
AI247 | Volt-Watt Reference Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 0.1 | 0 | Volts | DVWC1.MMXN.Vol | 0 |  | Volt-Watt | C: For Function | M
AI248 | Volt-Watt Curve Index. Index of the Volt-Watt curve that should be used by the mode. If zero, then direct paramters are used. | 2 | 0 | 2147483647 | 1 | 0 | n/a | DVWC1.VWCrv | 0 | AO173 | Volt-Watt | C: For Function | M
AI281 | Constant VArs Reactive Power Target. Percentage of maximum reactive power. | 2 | -1000 | 1000 | 0.1 | 0 | Percent | DVAR.VArTgtPct | 0 | AO203 | Const VArs | C: For Function | M
AI288 | Constant Power Factor Setpoint - Generation / Discharging | 2 | 0 | 100 | 0.01 | 0 | None | DFPF.PFGnTgt | 0 | AO210 | Constant PF | C: For Function | M
AI328 | Curve Edit Selector | 2 | 1 | 2147483647 | 1 | 0 | n/a | DGSMn.InCrv | 1 | AO244 | Curve | M | C: See clause 1.7
AI329 | Curve Type. Enumeration: <0> Curve disabled <1> Not applicable / Unknown <2> Volt-Var <3> Frequency-Watt <4> Watt-VAr <5> Voltage-Watt <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation Low Voltage ride-through curves <11> LVRT Must Trip <12> LVRT Momentary Cessation High Frequency ride-through curves <13> HFRT Must Trip <14> HFRT Momentary Cessation Low Frequency ride-through curves <15> LFRT Must Trip <16> LFRT Momentary Cessation | 2 | 0 | 20 | 1 | 0 | Enum | DGSMn.ModTyp | 0 | AO245 | Curve | M | C: See clause 1.7
AI330 | Curve Number of Points | 2 | 0 | 100 | 1 | 0 | n/a | FMARn.PairArr.NumPts | 0 | AO246 | Curve | M | C: See clause 1.7
AI331 | Independent (X-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / Unknown <4> Time <29> Voltage <33> Frequency <38> Watts <23> Celsius Temperature <100> Price in hundredths of local currency <129> Voltage as a percent of nominal voltage (VRef) <133> Frequency as a percent of nominal frequency <138> Percent Watts <233> Frequency Deviation <234+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.IndpUnits | 0 | AO247 | Curve | M | C: See clause 1.7
AI332 | Dependent (Y-Value) Units for Curve. Enumeration: <0> Curve is not defined <1> Not applicable / unknown <2> VArs as percent of max VArs (VARMax) <3> VArs as percent of max available VArs (VArAval) <4> Vars as percent of max apparent Watts (VAMax) - used in IEEE 1547 <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor in EEI notation <8> Volts as a percent of nominal voltage (VRef) <9> Frequency as a percent of nominal frequency <29> Voltage <33> Frequency <38> Watts <99+> Other | 2 | 0 | 255 | 1 | 0 | Enum | FMARn.DepRef | 0 | AO248 | Curve | M | C: See clause 1.7
AI333 | Curve Point 1 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.xVal | 0 | AO249 | Curve | M | C: See clause 1.7
AI334 | Curve Point 1 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.1.yVal | 0 | AO250 | Curve | M | C: See clause 1.7
AI335 | Curve Point 2 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.xVal | 0 | AO251 | Curve | M | C: See clause 1.7
AI336 | Curve Point 2 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.2.yVal | 0 | AO252 | Curve | M | C: See clause 1.7
AI337 | Curve Point 3 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.xVal | 0 | AO253 | Curve | M | C: See clause 1.7
AI338 | Curve Point 3 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.3.yVal | 0 | AO254 | Curve | M | C: See clause 1.7
AI339 | Curve Point 4 X-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.xVal | 0 | AO255 | Curve | M | C: See clause 1.7
AI340 | Curve Point 4 Y-Value | 2 | 0 | 100 | 1 | 0 | Varies | FMARn.PairArr.CrvPts.4.yVal | 0 | AO256 | Curve | M | C: See clause 1.7
AI536 | System Meter Frequency | 3 | 0 | 70000 | 0.001 | 0 | Hz | SYS.MMXU.Hz | 0 |  | Monitoring | M | M
AI537 | System Meter Active Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | SYS.MMXU.TotW | 0 |  | Monitoring | M | M
AI541 | System Meter Reactive Power | 3 | -2147483648 | 2147483647 | 1 | 0 | Vars | SYS.MMXU.TotVAr | 0 |  | Monitoring | M | M
AI547 | System Meter Phase A Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsA.mag | 0 |  | Monitoring | M | M
AI548 | System Meter Phase A Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsA.ang | 0 |  | Monitoring | M | M
AI549 | System Meter Phase B Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsB.mag | 0 |  | Monitoring | M | M
AI550 | System Meter Phase B Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsB.ang | 0 |  | Monitoring | M | M
AI551 | System Meter Phase C Volts | 3 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.PhV.phsC.mag | 0 |  | Monitoring | M | M
AI552 | System Meter Phase C Angle | 3 | 0 | 3600 | 0.1 | 0 | Degrees | SYS.MMXU.PhV.phsC.ang | 0 |  | Monitoring | M | M
AI553 | System Meter Average Line to Line Voltage | 1 | 0 | 2147483647 | 0.1 | 0 | Volts | SYS.MMXU.AvPPVPhs | 0 |  | Monitoring | M | M
AI554 | System Meter Current A | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsA.mag | 0 |  | Monitoring | M | M
AI555 | System Meter Current B | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsB.mag | 0 |  | Monitoring | M | M
AI556 | System Meter Current C | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | SYS.MMXU.A.phsC.mag | 0 |  | Monitoring | M | M
AI590 | Frequency-Watt Droop High Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DHFW3.WGra | 0 | AO480 | Droop Freq-Watt | C: For Function | M
AI591 | Frequency-Watt Droop Low Discharging / Generating Gradient | 2 | 0 | 2147483647 | 0.001 | 0 | W per Hz | DLFW3.WGra | 0 | AO481 | Droop Freq-Watt | C: For Function | M
AI592 | High Frequency-Watt Droop Minimum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DHFW3.WMin | 0 | AO482 | Droop Freq-Watt | C: For Function | M
AI593 | Low Frequency-Watt Droop Maximum Active Power | 2 | 0 | 2147483647 | 0.001 | 0 | Watts | DLFW3.WMax | 0 | AO483 | Droop Freq-Watt | C: For Function | M
AI619 | Active Power Limit Maximum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMX.WLimSpt | 0 | AO509 | Active Power Limit | C: For Function if BI113 = 1 | M
AI620 | Active Power Limit Minimum (Pos = Generation, Neg = Consumption) | 2 | -2147483648 | 2147483647 | 1 | 0 | Watts | DWMN.WLimSpt | 0 | AO510 | Active Power Limit | C: For Function if BI113 = 1 | M
AI621 | Constant Vars using vars as unit | 2 | -2147483648 | 2147483647 | 1 | 0 | Vars | DVAR.DVar.Tgt | 0 | AO511 | Constant Vars | C: For Function if BI115 = 1 | M

## CTR
DNP3 Point Index | Name / Description | Default Class Assigned to Counter Events | Frozen Counter Exists (Yes or No) | Default Class Assigned to Frozen Counter Events | IEC 61850 | Additional Information |  |  | EUT Capabilities
[5 empty] | IEC61850UniqueString | Purpose/Mode/ Function | Mandatory for IEEE 1815.2: M, C (plus specific condition), or blank | Mandatory for 1547-2018: M or blank | Supported by EUT? (Mark “x”)

## System Diagrams
Naming of Data Objects